INDEX

| S. No. | NAME OF THE 220 KV SUB-STATION | PAGE NO. |  | S. No. | NAME OF THE 220 KV SUB-STATION | PAGE NO. |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | BTPS | 3-4 |  | 15. | NARELA | 32-33 |
| 2. | DSIIDC BAWANA | 5-6 |  | 16. | OKHLA | 34-35 |
| 3. | GAZIPUR | 7-8 |  | 17. | PAPANKALAN-I | 36-37 |
| 4. | GEETA COLONY | 9-10 |  | 18. | PAPANKALAN-II | 38-39 |
| 5. | GOPALPUR | 11-12 |  | 19. | PARK STREET | 40-41 |
| 6. | GT STATION | 13-14 |  | 20. | PATPARGANJ | 42-43 |
| 7. | I.P.EXTN. (PRAGATI) | 15-16 |  | 21. | ROHINI | 44-45 |
| 8. | I.P. STATION | 17-19 |  | 22 | RPH | 46-48 |
| 9. | KANJHAWLA | 20-21 |  | 23. | SARITA VIHAR | 49-50 |
| 10. | KASHMERE GATE | 22-23 |  | 24. | SHALIMAR BAGH | 51-52 |
| 11. | LODHI ROAD | 24-25 |  | 24. | SUBZI MANDI | 53-54 |
| 12. | MEHRAULI | 26-27 |  | 25. | SOUTH OF WAZIRABAD | 55-56 |
| 13. | NAJAFGARH | 28-29 |  | 26. | VASANT KUNJ | 57-58 |
| 14 | NARAINA | 30-31 |  |  |  |  |

BADARPUR THERMAL POWER STATION

| Generation capacity of the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 220kV feeders from the station |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| Unit I 95MW Unit II 95MW Unit III 95MW Unit IV 210MW Unit V 210MW ------------------------------- TOTAL – 705MW |  | 220 Mehrauli Ckt-I 220 Mehrauli Ckt-II 220 Okhla Ckt-I 220 Okhla Ckt-II 220 S Vihar Ckt-I 220 S Vihar Ckt-II 220kV Alwar Ckt 220kV Blb. Garh-I 220kV Blb. Garh-II 220kV Noida Ckt | In case of grid failure BTPS should get islanded with the house load of Okhla. In case failure of island start up power should be availed from GT station of IPGCL on priority or In case GT supply is not available start up power should be availed through Faridabad Gas-Samay pur-Ballabhgarh-BTPS Ckt | 220 Mehrauli Ckt-I 220 Mehrauli Ckt-II 220 Okhla Ckt-I 220 Okhla Ckt-II 220 S Vihar Ckt-I 220 S Vihar Ckt-II 220kV Alwar Ckt 220kV Blb. Garh-I 220kV Blb. Garh-II 220kV Noida Ckt |  |  |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.14 Hrs. on 08.07.2009

SINGLE LINE DIAGRAM OF BTPS STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs. on 08.07.2009

DSIIDC BAWANA 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. TOTAL – 200 MVA | ON ON | 220 Bawana- DSIDC Bawana D/C T/L. 220 Narela- DSIDC Bawana D/C T/L. | (i) In case of outage of Bawana source back-feed can be taken from 220kV Narela. (ii) Similarly in case of breakdown of one 100MVA Transformer load can be met through other Transformer | 66/11kV 20MVA Tx-III |  |  |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF DSIIDC BAWANA 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs. on 08.07.2009

GAZIPUR 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. Total – 200 MVA | 50 51 101 MW | 220 kV BTPS-Noida-Gazipur Circuit. 220 kV Sahibabad-NOIDA-Patparganj T-Off to be energized on 23.5.07 as duplicate source. | The main incoming supply is from BTPS through 220 kV Noida-Gazipur Circuit. In case of outage of circuit, load can be diverted on 66 kV network depending upon the loading conditions of 220/66 kV 100 MVA Transformer No.1 and 2 at Patpatganj. | 66kV Feeders 1.Kondli –I&II (50, 46MW) 2.Vivek Vihar- I&II (OFF) 3*. 66/11kV One 20 Pr.Tr. (5MW) | - Part load on Patparganj via Mayur Vihar Ph-II and part load via Vivek Vihar 220kV Patparganj From Patparganj via Vivek Vihar | 1 DDA Flat Gazipur 2 Fish Market-I 3 Fish Market-II 4 Khichripur S/Stn-III 5 Telco-I 6 Telco-II 7 Telco-III 8 SFS Taj Apartment 9 SFS DDA Flat |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 14.12 Hrs. on 08.07.2009

- In case of complete blackout of the station, 66kV bus of Gazipur can be energised by having supply from 66kV Vivek Vihar station and load of this station can be met.

SINGLE LINE DIAGRAM OF GAZIPUR 220 KV SUB-STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

GEETA COLONY 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 33kV feeders Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I 220/33 kV, 100 MVA – II. Total – 200 MVA Note : N-I criteria for transformation capacity holds good for the station. | 39 MW 58 MW 97 MW | 220kV Wazirabad-Geeta Colony Ckt –I&II and Geeta Colony-Patparganj Ckt-I & II. | The main incoming supply is from Wazirabad-II, however, in case of failure of supply from Wazirabad alternate supply from Patparganj is available depending on load conditions. Similarly in case of failure of one 100MVA transformer major part load can be taken on 2nd transformer and part load (33 kV Geeta Colony and Shakarpur to be diverted to PPG). In case of total blackout loads on 33kV can be transferred as per arrangement shown in Col. V and VI. | 33kV Feeders i). Kailash Nagar I (24 MW) ii). Kailash Nagar II (9 MW) iii). Kanti Nagar I (13MW) iv). Kanti Nagar II(9 MW) v). Geeta Colony I (15 MW) vi). Geeta Colony II(9MW) vii). Sakarpur(18MW) | i) Seelampur ii) Karkadooma Grid iii) Patparganj Grid iv) Patparganj Grid | NIL |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF GEETA COLONY 220 KV SUB-STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

GOPALPUR 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66/33kV feeders and 66/11kV & 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I. 220/33kV, 100 MVA – II. 220/66 kV, 100 MVA – I. Total – 300 MVA | 51 43 38 132 MW | i) 220 kV D/C from Mandola. ii) 220 kV D/C South of Wazirabad iii)Outgoing 220kV D/C to Subzi Mandi | In case of outage of Mandaula source supply to be taken on Wazirabad D/C line. | 66kV Feeders 1.Jahangirpuri Ckt.-I&II (19,19MW) 33kV Feeders 1.Indira Vihar Ckt.- I (20 MW) 1. Indira Vihar Ckt.- II (23 MW) 3.Civil Line Ckt.(ON) 4.DIFR (ON) 5.Wazirabad I (8MW) 6. Wazirabad II (ON) 7.Azadpur I(14MW) 8.Azadpur II(14MW) 9. Two 33/11kV 16 MVA Pr. Trs. (9,6MW) | - Through Rohini-Pitampura & Narela-Jahagirpuri 66 KV circuits. By charging 220 KV bus through 66 KV Narela-Jahangirpuri-Gopalpur 66 KV circuit. Kashmere Gate Kashmere Gate Through 11 kV system. Jahangirpuri Kashmere Gate through Civil Lines. | 1 Mukherjee Nagar Complex 2 Wazirabad-I 3 Rainey Well 4 BPN Colony 5 Gas Plant 6 S.A. Bandh 7 Gandhi Vihar A Block 8 Wazirabad-II 9 Jagatpur |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF GOPALPUR 220 KV SUB-STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

GT STATION

| Generation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of complete outage of the station. | Details of 66kV feeders Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| Unit – 1 30MW Unit – 2 30MW Unit – 3 30MW Unit – 4 30MW Unit – 5 30MW Unit – 6 30MW STG - I 30MW STG - 2 30MW STG – 3 30MW 270MW | Nil | 220/66kV 160MVA Tx 220/66kV 100MVA Tx | In case of blackout GT’s should black start and extend supply tot he grid through 220/66kV 100MVA ICTs to feed the start up supply of generating units within Delhi Based on the advice of SLDC important load should be normalized. | 66kV Feeders 1. 66kV DMRC Ckt-I 2. 66kV DMRC Ckt-I 3. 66kV Vidyut Bhawan Ckt-I 4. 66kV Vidyut Bhawan Ckt-II 5. 66kV School Lane Ckt-I 6. 66kV School Lane Ckt-II |  | Nil |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF GT STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs. on 08.07.2009

PRAGATI (I. P. EXTENSION) 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of Important Load fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. Total – 200 MVA | 20 20 40 MW | 1.Sarita Vihar– IP Extn. D/C 2. G.T. Stn.– IP Extn. through 66/220 kV 100 MVA Transformers. 3.220 kV Pragati – IP Extn. D/C 4. 220 kVI.P. – IP Extn. D/C | IP Extn. is an important link between various generating stations. One 220 kV Bus is charged from BTPS, Pragati and G.T. The other bus is charged from I.P., Pragati STG. Normally the load of Park Street is taken on BTPS and Bus coupler at IP Extn.is kept open to avoid over-loading of 220 KV Circuits. In case of outages of any of the circuits, the generation of GT/Pragati is shifted from one Bus to other as per Load Generation Balance. | 220kV Park Street Ckt.-I & II (In case of failure of 220kV supply from I.P.Extn. , Part load of Park Street Stn. can be met on 66kV Network through 66kV Ridge Valley Stn.) | Ridge Valley Ckt.-I & II (on 66kV) | No 11kV Feeder |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF PRAGATI (I. P. EXTENSION) 220 KV SUB-STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

I. P. STATION

| Generation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of complete outage of the station. | Details of 33kV feeders and 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| Nil | Nil | 220kV Pragati Ckt-I 220kV Pragati Ckt-II 220kV PPG Ckt-I 220kV PPG Ckt-II 220 kV RPH Ckt-I 220 kV RPH Ckt-I | In case of failure of 220kV supply startup power for RPH should be ensured through Pragati Ckts or through Patpargan Ckts as per the advise of SLDC after switching of all 33kV feeders. Based on the advise of SLDC important load should be normalized. The entire normalization of the station is done as per the advise of SLDC. | 33kV Feeders 1. Nirman Bhawan-I 2. Nirman Bhawan-II 3. Kilokri 4. Electric Lane-I 5. Electric Lane-II 6. Lajpatnagar 7. Tilak Marg 8. Exhibition Gr-I 9. Exhibition Gr-II 10. Nizamuddin 11. Delhi Gate 12. Kamla Market-I 13. Kamla Market-II 14. GB Pant 15. Defence Colony 16. Kilokri 17. Cannaught Place 18. IG Stadium-I 19. IG Stadium-II 20. Minto Road 21. Kilokri 22. Cannaught Place 23. Kilokri 24 Kilokri |  |  |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF IP STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs. on 08.07.2009

SINGLE LINE DIAGRAM OF IP STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs. on 08.07.2009

KANJHAWALA 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. Total – 200 MVA | 11MW 27 MW 38 MW | T-Off 220 kV Bawana – Najafgarh Circuit No.I | In case of outage of 220 kV circuit, there is no alternate source at 220 KV or 66 KV level. Loads can be transferred only on 11 KV by N.D.P.L. | 1. 66/11kV 20MVA Pr.Trf. I (10 MW). 2. 66/11kV 20MVA Pr.Trf. II (10 MW). 3. 66kV Pooth Khurd (18MW) 4. 66kV Clear Water Bawana S/Stn. (ON) 5. DMRC (ON) | Bawana 220/66 KV through Bawana-Bawana clear water works. 66kV Clear Water Bawana S/Stn. 66kV Pooth Khurd | 1 U/G Kanjhawala 2 Ghewra 3 O/H Kanjhawala 4 S.O.S. Bawana 5 ABC Punjab Khore 6 ABC Kanjhawala 7 O/H Rani Khera 8 ABC Rani Khera |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF KANJHAWLA 220 KV SUB-STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

KASHMERE GATE 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 33kV feeders fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I. 220/33 kV, 100 MVA – II. Total – 200 MVA | 44 - 44 MW | South of Wazirabad – Kashmere Gate D/C. O/G DMRC Circuit I & II | In case of outage of one circuit, the load can be met through other circuit. In case of outage of both the circuits, the part load can be met through 33 kV network with the possibilities of back feeding as per col (v) and (vi). The load of Metro is to be diverted to Rohini – Rithala 66kV STN. | 33kV feeders 1.Fountain Ckt.I ( ON) 2. Civil Lines I (10MW) 3. Civil Lines II (6MW) 4.Jama Masjid (ON) 5.Town Hall (ON) 6. 20MVA, 33/11kV T/F (10 MW) 7. 16MVA, 33/11kV T/F (9MW) | -RPH - Gopalpur - Gopalpur -RPH -RPH 33kV feed can be taken from RPH via Civil line grid to meet these loads. | 1 DMRC 2 Asaf Ali Hospital 3 Bela Road 4 Electric Cremetorium 5 ISBD Flyover-I 6 ISBT Flyover-II 7 Ludlo Castle 8 Hamilton Road 9 Jindal Hospital 10 Metcalf House 11 New Kashmiri Gate 12 GPO |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF KASHMERE GATE 220 KV SUB-STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

LODHI ROAD 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 33kV feeders and 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I. 220/33kV, 100 MVA – II. Total – 200 MVA | 73 83 156 MW | 220 kV Maharani Bagh – Lodhi Road Circuit No. I & II. | In case of outage of one circuit the load can be taken on the other circuit through respective 220/33 KV transformer and part load can be taken from 33 KV Vidyut Bhawan-Lodhi Road circuit depending upon the load condition of 66 KV GT-Vidyut Bhawan circuits and 66/33 KV 50 MVA transformer at Vidyut Bhawan. In case of outage of both the 220 KV circuits the essential load can be met through 33 KV Vidyut Bhawan- Lodhi Road circuit depending upon the loading conditions mentioned above and load of other area being fed from Lodhi Road is back-fed wherever possible as per col(v) and (vi). | 33kV Feeders 1.Defence Colony Ckt.-I (ON) 2.Defence Colony Ckt.-II (18MW) 2. India Habitat – I(ON) &II (4 MW) 3.HUDCO (20MW) 4.NDSE CKT.II (8MW) 5.Nizamuddin(9MW) 6.Vidyut Bhawan(16MW) 7.Exhb. Ground-II (14 MW) 8. Lajpat Nagar Ckt-I (11 MW) 9. Lajpat Nagar Ckt.II (22 MW) 10. 33/11kV Pr. Trs No.I 20MVA.(9 MW) No.II 20MVA.(9MW) No.I 16MVA.(8 MW) No.II 16MVA.(8 MW) | (1) T-off from Kilokri-Medical feeder (2) IP-Defence Colony feeder - Single source RKP-Kilokri Ckt Kil-Medical Ckt - IP Station - GT Station - Exhb.Ground-I - 220kV Okhla through East of Kailash --do— - IP Station/ Okhla feeder | 1 Scope Bldg. 2. NBCC 3. Scope Complex-15 4 Defence Colony 5. MS-I 6. Stadium R-1 7 Cabinet Sectt 8. Instt. Area 9. Shan Ngr-1 10 Stadium R-7 11 Unido S/Stn 12. Sewage Pump. Stn 13. Defence Colony 14. DOE-II 15 Shan Naar-II 16 Lodhi colony compl. Center 17 DOE-I 18 Scope Bldg-16 19 NBCC East Block 20 NSO-II 21 Telephone Exchange |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF LODHI ROAD 220 KV SUB-STATION

**Note NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

MEHRAULI 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/66 kV, 100 MVA – III. TOTAL – 300 MVA | 76 73 73 222MW | 1.220 KV BTPS-Mehrauli D/C T/L. 2. 220 KV Bamnauli- Mehrauli D/C T/L. 3. 220 KV Mehrauli – Vasant Kunj D/C T/L. | Normally 220/66 KV 100 MVA Transformers are fed from 220KV BTPS circuits. 220 KV Bamnauli No.1 feeds 220 KV Vasant Kunj and 220 KV Bamnauli No.2. i) In case BTPS circuits get overloaded one 100MVA Pr. Transformer can be taken on Bamnauli Ckt –II. In case of complete outage of the station, the load of 66kV grids shall be fed as per the arrangement shown under col. (v) and (vi) (ii) In case of outage of one 100MVA Pr. Transformer the load can be taken on other two transformers and some load of the Stn. can be shifted as per arrangement shown under col.(v) and (vi) . Priority of restoration Supply to the following feeders is to be restored on priority :- i)66 KV IAAI feeder. ii)66 KV Bijwasan circuits | 66kV Feeders 1. IOC (32MW) 2. Palam (ON) 3. V.Kunj ‘D’ Blk I (ON)&II (ON) 4. Malviya Nagar I(33 MW)&II (43MW) 5. C. Dot I&II (22MW, ON) 6. 66/11kV 20MVA (4MW) & 20MVA (5 MW) 7. Vasant kunj ‘C’ Block I(45MW) & II(45 MW) | -Palam -220kV Vasant Kunj --220kV Vasant Kunj -Okhla 220kV -Single Source Vasant Kunj --220kV | 1 Dera Bhati, 2 Andheria Bagh (1) 3 Vasant Kunj `A’ 4.Vasant Kunj `D’ 5. Andheria Bagh (2) 6 Fatehpur Beri |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF MEHRAULI 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

NAJAFGARH 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Trs. fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/66 kV, 100 MVA – III 220/66 kV, 100 MVA –IV. Total – 400 MVA | 70 70 70 70 280 MW | 220kV Bawana-Najafgarh D/C 220kV Bamnauli-Najafgarh D/C | Normally load of Najafgarh is kept on Bawana circuits. Bamnauli circuits are kept in OFF position. In case of outage of Bawana source, the load can be met through Bamnauli depending upon loading of 400/220kV ICT at Bamnauli. The possibilities of back feeding on 66kV level in case of black out of the station are shown in col. (v) & (vi). | 66kV Feeders 1.Matiyala Ckt-I&II (39MW,19MW) 2.Bodela –II Ckt-I&II (44MW, 46MW) 3.Nangloi (46MW) 4.Nangloi Water Works (48MW) 5.Jaffarpur Ckt.-I&II (20MW, 9MW) 6.Three 66/11kV 20MVA Pr.Tr. (11,15,11MW) | -Papankalan (via Pankha Road) - Paschim Vihar -Rohini220kV -Rohini220kV -Single Source - PPK-I / Bodella-I / Rohini | 1 Pump. Stn 2 Najafgarh 3 Chawla Trunk 4 Rama Park 5 Deenpur 6 DVB Colony 7 TP Kotla 8 Anaj Mandi 9 Nangli Sakrawati 10 Seven Panel 11 Kakrola |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF NAJAFGARH 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

NARAINA 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 33kV feeders and & 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I. 220/33 kV, 100 MVA – II 220/33 kV, 100 MVA – III. Total – 300 MVA | 44 59 103 MW | 220 kV Bamnauli-Naraina D/C | In case of outage of 220 kV circuits, the essential load of Naraina can be met on 33 kV network to the extent possible as shown in Col. (v) and (vi) | 33kV Feeders 1.Khebar Lane Ckt.-I&II (8MW, 6MW) 2.Rewari Line Ckt-I&II (35MW) 3.Kirbi Place Ckt.-I&II (7MW) 4.Inderpuri Ckt. (20MW) 5. DMS (23MW) 6.Two 33/11kV 16MVA Pr. Trs. (21MW) | -Ridge Valley -Papankalan 220kV -Single Source -Rewari Line -Inderpuri /Shankar road / Rohtak Road - Part load can be taken on Ridge Valley via Kheber Lane grid and balance to be transferred on 11kV network. | 1 Payal Zone Office 2 Magoo-I 3 Kirby Place-I 4 Gopi Nath Bazar 5 Brar Square 6 Kirbi Place-II 7 Naraina Vill. 8 Magoo-II 9 `A’ Blk Shopping Complex |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF NARAINA 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

NARELA 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66KV & 33kV feeders and 66/33kV and 66/11kV Pr. Trs. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/66 kV, 100 MVA – III. Total – 300 MVA 66/33 kV, 30 MVA Tx. | 77 74 51 202 MW 12 MW | 220 kV Mandola-Narela - D/C T/L 220 kV Bawana DSIIDC -Narela – D/C 220 kV Panipat-Narela Circuit I,II,III | Under normal arrangement one 220 kV Bus of Narela is on Mandola source and the other 220 kV Bus is kept on Panipat source. The load of 220 kV Rohtak Rd and 100 MVA Transformers at Narela is kept on Mandola bus. The load of 220 kV Rohini-Shalimar Bagh and 220/132 kV BBMB transformers is kept on Panipat Bus. In case of outage of any of the circuit from Mandola or Panipat the load is shifted to Bawana with minor shifting of load at 33kV or 66kV level as per col (v) and (vi). In case of failure of one 100MVA Tr. the load can be shifted to other two with minor adjustment as per col (v) and (vi) above. | 66kV Feeders 1.Jahangirpuri Ckt.-I & II (42,41 MW) 2. Badli Ckt.-I&II (16,15MW) 3. A 7Narela Ckt-I & II (37,37MW) 4. 20MVA, 66/11kV Pr. Trs (7,3MW) 33kV Feeders 1.AIR Khampur (12 MW) 2. Hyderpur (No Load) | - Part load on Gopalpur - Rohini - Single Source - Jahangirpuri - Shalimarbagh | 1 U/G Narela 2 DDA-5 3 Narela O/H 4 DDA B-4 5 Colony Transformer 6 Bawana 7 DSIDC 8 BBMB |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF NARELA 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

OKHLA 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66/33kV feeders and 66/11kV & 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA– II. 220/33 kV, 100 MVA – I. 220/33kV, 100 MVA– II. 220/33 kV, 50 MVA– I. 220/33kV, 50MVA– II. Total – 500 MVA | 84 82 66 66 24 24 346 MW | 220 KV BTPS-Okhla D/C T/L | (i) In case of failure of supply from BTPS, loads of 66kV and 33kV can be met through other sources to the extant possible as per arrangement shown in Col. (v) and (vi) (ii) In case of failure of one 220/66kV, 100MVA Pr. Tr. load can be met through other Tr. by shifting some of the load as per Col.(v) &(vi) (iii) In case of failure of any one 220/66kV Pr. Tr., load can be met through other available Trs. | 66kV Feeders 1.Malviya Nagar –I,II &III (38 MW,38MW,32MW) 2. Okhla-Ph-I Ckt-I&II (20MW,20MW) 33kV Feeders 1.Okhla Ph-II Ckt. I&II (19MW,18MW) 2. Nehru Place Ckt-I&II&IV 3.Masjid Moth 4. Tuglakabad 5. East of Kailash Ckt. 6. Alaknanda Ckt. – I&II 7. 66/11kV, 2Nos. 20MVA Pr. Trs.. 8. Balaji Ckt-I&II | - Mehrauli -Mohan Cooprative - Sarai Juliana - Masjid Moth - D.C. Saket - Malviya Ngr -Part load on Lajpat Nagar - Masjid Moth (T-OFF) | 1 DDA 2 Giri Nagar 3 Pocket-A10 Kalkajee Ext. 4. A-12 S/Stn 5. Alaknanda 6.giri Nagar-II 7 Pocket-A-18 Kalkajee Ext. 8 Tara Aptt. 9. Gobindpuri |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF OKHLA 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

PAPANKALAN – I 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/66 kV, 100 MVA – III 220/66 kV, 100 MVA – IV. Total – 400 MVA | 82 82 78 78 320 MW | 220 kV Bamnauli-Papankalan D/C Tower Line | In case of outage of one circuit, the load can be taken on other circuit. In case of outage of both the circuits, the essential loads can be met on 66 kV network from other sources as shown under Col-(v) and (vi) | 66kV Feeders 1.Bindapur Ckt-I&II (37,37MW) 2.G-II Ckt.-I&II (45, 45MW) 3.G-6 Ckt.-I&II (ON, 25MW) 4. Rewari Line (47MW) 5. Bodella-I (47MW) 6.Three 66/11kV 20MVAPr.Trs. (13,11,11MW) 7. DMRC Ckt-I&II | - Matiala (part load) - Rewari Line - Single Source - Naraina 220k - Paschim Vihar - Load can be transferred on 11kV System 7. PPK-II | 1 Sec-II Pappk. 2 Sec-10 Pappk 3 PP-I 4 Mahaluxmi 5 Manglapuri 6 Sec-19 7 NSIT 8 PP-II 9 Bengali Cly 10 Naseerpur 11 Palam Vill. 12 Sec-7 13 Evergreen 14 Vinodpuri 15 C-2 |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF PAPANKALAN-I 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

PAPPANKALAN – II 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA –I 220/66 kV, 100 MVA –II Total – 200 MVA | No Load 5 MW | 220 kV Bamnauli-Papankalan-II Ckt-I & II | In case of outage of one circuit, the load can be taken on other circuit. | 66kV Feeders 1.DMRC Ckt-I&II | - Pappankalan-I |  |

**Note : All loading are in MW and corresponds to 4408 MW at 16.12.49 Hrs.on 08.07.2009.

SINGLE LINE DIAGRAM OF PAPPANKALAN-II 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs. on 08.07.2009

PARK STREET 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66/33kV feeders and 66/11kV & 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/33 kV, 100 MVA – I. 220/33kV, 100 MVA – II. Total – 400 MVA | 58 4 56 62 180 MW | 220 KV IP Ext – Park street U/G D/C Line. | In case of outage of one cable circuit load of Ridge Valley, Shankar Road, Faiz Road, Motia Khan is diverted to other sources to the extent possible. In case of outage of both the 220 kV Circuits, essential load can be met through 66 kV Ridge Valley Park Street circuits. Possibilities of back feeding are shown in col. (v) & (vi). | 66kV Feeders 1.Ridge Valley – I&II 2.B.D. Marg –I&II 3. Shastri Park 33kV Feeders 1. Prashad Nagar 2. Shanker Road 3. Motia Khan – I&II 4. Nirman Bhawan 5. Faiz Road-I&II 6. Baird Road-I&II 7. Hanuman Road | - 220kV Vasant Kunj -Single Source -Prashad Ngr (on 33kV) - Rohtak Road -Ridge Valley - Minto Road - IP Stn. - Rohtak Road -Single Source -School Lane | No 11kV Feeders |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF PARK STREET 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

PATPARGANJ 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66/33kV feeders and 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| 220/66 kV, 100 MVA– I. 220/66 kV, 100 MVA– II. 220/33 kV, 100 MVA– I. 220/33kV, 100 MVA– II. 220/33 kV, 50 MVA– I. 220/33kV, 50MVA– II. Total – 500 MVA | 64 24 48 B/D 21 48 205MW | i) 220 kV Geeta Colony-Patparganj D/C T/L ii)220kV IP– Patpar Ganj D/C T/L iii)220kV Sahibabad – Patparganj D/C (kept open at Patparganj end) | Patparganj 220kV S/Stn. is the inter-linking S/Stn to keep IP, RPH & Pragati (one Unit and STG) in synchronism with Mandola supply. i) In case of outage of Geeta Colony circuits, if supply is available through 220 kV IP - Patpatganj Ckts, load is to be regulated depending upon availability of generation in this pocket. ii) If IP supply is also not available then all the loads (66/33 kV loads) should be thrown off and start up supply to be extended to Generation complex after availing supply from Mandola as per the advise of SLDC. The supply from Sahibabad is kept open at Patpatganj due to load restriction by UP on the circuit. Supply can be taken in emergency as per availability. | 66kV Feeders 1.Vivek Vihar-I&II (114MW) 2. Khichripur (Off) 3. GH-I (38) 33kV Feeders 1. Preet Vihar (19MW) 2. Geeta Colony (17MW) 3. Guru Angad Nagar –I & II (29MW) 4.Karkardooma- I & II (16MW) 5. CBD Shahdra (14MW) 6. Kailash Nagar /Shakar Pur (13MW) 7. Scope Building- I &II (3.5MW) 8. One 33/11kV 20MVA Pr. Tr. One 33/11kV16MVA Pr. Tr. (16.5MW) | - Part load from Gazipur - Gazipur - Gazipur - CBD Shahdra /Vivek Vihar - Guru Angad Nagar - Geeta Colony - Vivek Vihar - Preet Vihar - Seelampur - Single Source | 1 National Dairy 2 Staff Qrts-II 3 Comml. Blk 4 Ganesh Ngr Complex 5 Shakarpur Kiosk 6 National Dairy-II 7 Nirman Vihar Flats 8 Six Pole Structure 9 Preet Vihar 10 Staff Qrts-II 11 Rainey Well |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF PATPARGANJ 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

ROHINI 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/66 kV, 100 MVA – III. 220/66 kV, 100 MVA – III. Total – 400 MVA | 87 87 90 87 351 MW | 220 kV Shalimar Bagh – Rohini D/C (172 MW) (ii) 220kV Bawana – Rohini D/C | In case of outage of one circuit, the load of Rohini station can be met on other circuit. In case of outage of both the circuits, essential load can be met through 66 kV network from other sources. Priorities are given to feed Metro through Rohini-Rithala Circuit alternatively load of Metro can be met from Kashmere Gate. In case of failure of one 100MVA Power Transformer the load can be met through the other two by shifting some of the stn. load at 66kV level as shown under col. (v) and (vi) | 66kV Feeders 1.Rohini –VI Ckt.-I&II 2.Rohini –V Ckt.-I&II 3.Rohini –IV Ckt.-I, II, III & IV 4.Rohini-22 S/C 5.Rohini-23 S/C 6.DMRC –I&II 7.Two 66/11kV 20MVA Pr.Trs. | - Badli - Pitampura-I via Rohini-III - --do-- - Single Source - Single Source - Single Source (DMRC can change supply to Kashmere Gate) | 1 6/11 Rohini 2 DMB-I 3 8/11 Rohini 4. 480 SFS-I 5 NDPL Cly 6 Prahaladpur 7 DVB Cly 8 DMB-II 9 480 SFS-II 10 SPS DDA 11 Sec-25 12 STF MCD |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF ROHINI 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

RPH STATION

| Generation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of complete outage of the station. | Details of 33kV feeders and 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| Unit – I 67.5MW Unit – I 67.5MW 135MW | Nil | 220kV IP Ckt-I 220kV IP Ckt-II | In case of blackout start up supply should be availed through IP Ckts. as per the advise of SLDC after switching of all 33kV feeders. The entire normalization of the station is done as per the advise of SLDC. | 33kV Feeders 1. U/G Lahori Gate I&II 2. U/G Jama Masjid I&II 3. IG Stadium 4. G. B. Pant 5. Fountain 6. Minto Road 7. Town Hall 8. Kamla Market |  |  |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF RPH STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF RPH STATION

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of all time Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SARITA VIHAR 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. Total – 200 MVA Note :- (i) N-1 norm hold good for the station | 54 No Load 54 MW. | 1. 220 kV BTPS – Sarita Vihar D/C. 2. 220 kV IP Extn-Sarita Vihar D/C. | Sarita Vihar is the Linking Stn of BTPS and IP Ext (Pragati & GT Stn). In case of supply failure from BTPS, if supply is available from Mandola up to IP Ext through 220kV Mandola - Patparganj-IP-IP Extn link the same can be extended up to Sarita Vihar with regulation of load. The Mathura Road 66 kV sub-station is also fed though 66 kV Sarita Vihar-Mathura Road circuit No. I & II. In case of failure of one 100 MVA Tr complete load can be taken on the 2nd Transformer. In case of complete black-out, load of 2 Nos 66/11kV Pr. Trs can be met from 66kV Okhla Phase-I Ckt-I via 66kV Mathura Road – Mohan Cooperative S/Stns. | 66kV Feeders 1. Mathura Road Ckt.-I&II (41MW) 2. 66/11kV Two Nos. 20MVA Pr. Trs. (13 MW) | From 66kV OKHLA Ph–I Stn via Mohan Cooperative S/Stn From 66kV Okhla Ph-I via Mathura Road – Mohan Cooperative S/Stn. | 1. Jaitpur 2. Sewage Pump 3. Sourav Vhr 4. S/Stn-22 Sarita Vihar 5 Ali Village 6. America Express 7. IOC 8. S/Stn-21 Sarita Vihar |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF SARITA VIHAR 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

SHALIMAR BAGH 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 33kV feeders and 33/11kV Pr. Tr. Fed from the station and Loadings | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I. 220/33 kV, 100 MVA – II. Total – 200 MVA Note:- CWO for 3rd 100 MVA Transformer already stand issued. Transformer on order | 76 73 149 MW | 220 kV Bawana-Shalimar Bagh Ckt- I&II (149 MW) 220 kV Rohini- Shalimar Bagh Ckt-I&II (176 MW) | In normal course Bawana 220 kV feeder and Rohini feeders are kept on 220 kV Bus-I while Bawana circuit and both 100 MVA transformers are kept on 220kV bus-II In case of outage of any one source, load can be met through other source by diverting some of the 33kV station load to other sources as shown under vol (v) and (vi). In case of outage of one of the 100 MVA T/F load can be met through IInd T/F by transferring some of 33kV loads as shown in column (v) and (vi) | 33kV Feeders 1.Wazirpur –II CktsI,II,III And IV 85 MW 2. Hyderpur Ckt.I,II 11.5MW 3.S.G.T. Nagar Ckt. 11.5MW 4. Rani Bagh I,II 18MW 5. 33kV SMB S/Stn. 9.5MW 6. 33/11kV 20MVA 14MW Pr. Tr. 7.33/11kV 16MVA No Load Pr. Tr. | -Part load on Azadpur - Narela - Jahangirpuri - Single Source - Azadpur via Wazirpur –II Part load can be transferred on 11kV --do-- | 1. KU PPR 2 Sewage Pump 3 Badli-II 4 O/D Dispensary 5 Prashan Vhr 6 Badli-I 7 Booster Pump 8 Hyderpur Dispensary 9 Pitampura 10 11B SMB 11 MTD 12 FU Feeder 13 10 Blk SMB |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF SHALIMAR BAGH 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

SUBZI MANDI 220KV SUB-STATION

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of complete outage of the station. | Details of 33kV feeders and 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/33 kV, 100 MVA – I. 220/33 kV, 100 MVA – II. Total – 200 MVA Note ; N-I norms holds good for the station. | 35 22 57 MW | 220 kV Gopalpur-Subzi Mandi D/C T/L. ACSR Zebra conductor Capacity : 200 MW each circuit. | In case of outage of both 220 KV circuits or both the 220 KV Transformers. Load of 33 KV grids shall be back-fed as per arrangement shown in (v) & (vi). Load of 33/11 KV Transformers will be met through 33 KV feeders from Civil lines. Since B.G. road station is on single source, load will be transferred by BSES at 11 KV level. | 33kV Feeders 1.Shakti Nagar (11 MW) from---------- 2.Civil Line from ------ 3.Gulabi Bagh (11 MW) from---------- 4.B.G. Road Ckt.-I&II (23 MW) from --------- 6. Tripolia 33 KV station. 5. Two No. 33/11kV 16MVA Pr.Trs. (14 MW) from---------- | - Azadpur - Kashmere Gate - Shahzada Bagh Through 33 kV Rohtak Road-Shazadabagh- Subzi Mandi link. Through Azadpur-GT Karnal Road-Tripolia link. -Civil line ckt. | 1 Delhi School 2 Kabir Basti 3 Parag Ice Factory 4 Hindu Rao Hospital 5 B. G. Road 6 Azad Mkt 7Palace Cinema 8 K.K. College 9 Subzi Mandi 10 Narbada Cold Storage 11 New Court 12 St. Stephen College |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF SUBZI MANDI 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

SOUTH OF WAZIRABAD 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66/33kV feeders and 66/11kV & 33/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. 220/66 kV, 100 MVA – III. Total – 300 MVA | 44 44 42 137 MW | 1. 220kV Mandola-SOW Ckt. I,II,III & IV 2. 220kV Gopalpur-SOW Ckt. I&II 3. 220kV Wazirabad-Geeta Colony Ckt-I&II. 4. O/G 220kV Kashmiri Gate – SOW Ckt.I&II. | Main source is from 400kV Mandola sub-station. In case of outage of this source the load can be shifted on Gopalpur depending upon load conditions at Gopalpur. In case of outage of both Mandola and Gopalpur sources the load can be shifted to Geeta Colony depending upon load conditions at Geeta Colony. | 66kV Feeders 1. 66kV Yamuna Vihar No. I & II (ON) 2. 2Nos. 66/11kV 20MVA Pr.Trs. (9,11MW) 3. Shastri Park I & II (16,16MW) 4. Ghonda I & II (45,46MW) | Bhagirathi Seelampur on 33kV Bus charge Vivek Vihar via Nand Nagri | D-Blok Gamri Tukhmeerpur Bhajanpura B Blk Sonia Vihar WTP-I Sonia Vihar Raw Water Sadatpur 3 ½ Pusta Vijay Colony Wazirabad Switching Stn-2 Moni Baba Mandir 10. Shahdra Bandh Sonia Vihar WTP-II Sonia Vihar WTP-III |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF SOUTH OF WAZIRABAD 220KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs.on 08.07.2009

VASANT KUNJ 220KV Sub-station

| Transformation Capacity available at the station | Loading in MW** | Feeding arrangement of the station | Restoration procedures in case of blackout | Details of 66kV feeders and 66/11kV Pr. Tr. Fed from the station | Possibilities of back-feeding from | Name of 11kv feeders Emanating from the station |
| --- | --- | --- | --- | --- | --- | --- |
| (i) | (ii) | (iii) | (iv) | (v) | (vi) | (vii) |
| 220/66 kV, 100 MVA – I. 220/66 kV, 100 MVA – II. TOTAL – 200 MVA | 67 65 132 MW | 220 Mehrauli – Vasant Kunj D/C T/L. | (i) In case of outage of Mehrauli source back-feed can be taken from Ridge Valley at 66 KV level as per capacity available, and essential loads can be met. PALAM is to be given priority. The possibility of meeting other load at 66kV level is shown in col. (v) & (vi) (ii) Similarly in case of breakdown of one 100MVA Transformer load can be met through other Transformer by diverting some of the 66kV load as per col (v) and (vi) | 66kV Feeders 1. V.Kunj ‘D’ Blk-I&II (12,12MW) 2. V.Kunj ‘C’ Blk- I&II ( 3. Ridge Valley– I&II 4 66/11 kV Two Nos. 20MVA Pr.Trs. | - Mehrauli - Mehrauli - Park Street - Mehrauli via Vasant Kunj ‘C’ Block | 1 C-8 S/Stn-1 2. Airport Authority 3. Spinal Injury Hospital 4 S/Stn-5. C-9 5 S/Stn-1 C-9 6 AB Hotel 7 Mahipalpur 8 Nangal Dairy 9 Vasant Kunj-II C-8 10 Rangpuri |

**Note : Loading on the Transformers in MW has been taken at the time of occurrence of Peak Demand of 4408 MW at 16.12.49 Hrs.on 08.07.2009

SINGLE LINE DIAGRAM OF VASANT KUNJ 220 KV SUB-STATION

NOTE : ALL LOADINGS ARE IN MW AND CORRESPONDS TO THE OCCURRENCE OF PEAK DEMAND OF 4408 MW at 16.12.49 Hrs. on 08.07.2009

# Text boxes

FEEDING ARRANGEMENTS AND

EMERGENCY RESTORATION PROCEDURE,

& BACK FEEDING POSSIBILITIES

OF 220 KV SUB-STATIONS

OF

DELHI TRANSCO LIMITED.

DECEMBER  2009

220 KV BUS

Sahibabad

50 MW

100 MVA – I

220/66 KV

51MW

100 MVA – II

220/66 KV

BC

5 MW

20 MVA - I

66/11 KV

OFF

V. Vihar - II

50MW

Kondli-I

46 MW

Kondli-II

BC

Cap. Bank - I

66 KV BUS

11 KV BUS

DDA Flat

G. Pur

101MW

NOIDA

OFF

V. Vihar - I

Cap.

Bank - II

Fish

Mkt-I

Fish Mkt-II

K. Pur

S/S- III

Telco

I

Telco

II

Telco

III

SFS TA

SFS DDA Flat

220 KV BUS

39 MW

100 MVA – I

220/33 KV

BC

33 KV BUS

24 MW

Kailash Nagar-I

166 MW

SoW- I

128 MW

Patpar

ganj -I

58 MW

100 MVA – II

220/33 KV

BC

78 MW

SoW - II

19 MW

Patpar

ganj -II

9MW

Kailash Nagar-II

13 MW

Kanti Nagar-I

9 MW

Kanti Nagar-II

15 MW

Geeta ColonyI

9 MW

Geeta ColonyII

18 MW

Shakar

pur

220 KV BUS

51 MW

100 MVA – I

220/33 KV

BC

14MW

Azadpur-II

20MW

Indira Vihar I

33 KV BUS

11 KV BUS

M. Nagar

Comp.

Cap.

Bank

8MW Wazirabad-I

19MW

JJahangirpuri Ckt-II

Cap

Bank

ON

Civil Lines-I

9 MW

20 MVA - I

33/11 KV

Rainey Well

BPN Colony

Gas Plant

WB-I

SA

Bandh

GVA Block

WB-II

Jagat Pur

ON

WazirabadII

Mandaula- II

135MW

Subzi Mandi- I

37MW

Subzi

Mandi- I

(70MW)

43 MW

100 MVA – II

220/33 KV

BC

219MW

Jehangir Puri-I

66 KV BUS

38MW

100 MVA – I

220/66 KV

6MW

20 MVA-I

33/11 KV

16MW

Azadpur-I

ON

DIFR

23 MW

Indira ViharII

Mandaula- I

100 MW

220 KV BUS

100 MVA – II

220/66 KV

BC

Sarita Vihar Circuit

100 MVA – I

220/66 KV

Park Street Circuit - I

I. P. Stn

Ckt-I

Maharani Bagh Ckt

I. P. Stn

Ckt-II

Park Street Circuit - II

Gas Turbine

Circuit - I

Gas Turbine

Circuit - II

220/11 KV

Pragati Power Project

Circuit - II

220/11 KV

Pragati Power Project

Circuit - I

220 KV BUS

T-Off 220 KV Bawana – NJF Circuit – I

38 MW

11MW

100 MVA – I

220/66 KV

27MW

100 MVA – II

220/66 KV

BC

10 MW

20 MVA - I

66/11 KV

Spare

Pooth Khurd (18MW)

ON

C DOT-II

BC

10 MW

20 MVA - II

66/11 KV

ON

DMRC

20 MVAR Cap Bank

66 KV BUS

11 KV BUS

Local

Kanjhawla

Ghewra

Kanjhawla

SOS

Bawana

11 KV

I/C - II

Bus Sec Off

Spare

Punjab Khera

11 KV

I/C - I

Kanjhawla

Rani Khera

Rani Khera

Spare

5 MVAR Cap. Bank

220 KV BUS

100 MVA – II

220/33 KV

B/D

35 MW

100 MVA – I

220/33 KV

9 MW

16 MVA - I

33/11 KV

BC

33 KV BUS

11 KV BUS

SOW – K. Gate

Circuit – I

44 MW

1 MW DMRC- I

Civil

Line-II

6MW

8 MW

DMRC- II

FT – I

B/D

BC

Civil

Lines-I

10MW

ON

Jama Masjid

ON

Town Hall

11 KV DMRC

AA Ali Hosp.

Bela Road

10 MW

20 MVA - II

33/11 KV

Elect Crmt

ISBT

Fly Over II

Fly Over

Ludlow Castle

Hamilton Road

J. D. Hospital

MK House

New

K. G.

GPO

Local Transf.

SOW – K. Gate

Circuit – II

ON

83 MW

100 MVA – III

220/33 KV

33 KV BUS

11 KV BUS

73MW

100 MVA – I

220/33 KV

ON

Def Col-I

4MW

IHC-II

14 MW

EG- II

20 MW

HUDCO

22 MW

LPN -II

11MW

LPN-I

NDSE-I

16 MVA - II

33/11 KV

8 MW

9 MW

NIZMD

16 MW

V. B.

18 MW

Def Col-II

ON

IHC-I

Local trf

SR-I

SP

CS

MSO-I

OC

15 NO.

SCOPE

NBCC

17 No. SB

Sec-25

SR-7

SN-I

11 KV BUS

20 MVA – I , 33/11 KV

9 MW

20 MVA – II , 66/11 KV

9 MW

16 MVA - II

33/11 KV

8 MW

33 KV BUS

NDSE-II

8 MW

ON

FT - II

I. Area

UNIDO

SP

SN-II

LCC

DOE-I

16 No.

S. BLD

TE

MSO-II

SP

Cap. Bank

DOF

SP

SP

SP

220 KV BUS

76 MW

100 MVA – I

220/66 KV

73 MW

100 MVA – II

220/66 KV

BC

4MW

20 MVA - I

66/11 KV

BC

5 MW

20 MVA - II

66/11 KV

66 KV BUS

11 KV BUS

D. Bhati

AB - I

V.K. ‘A’

L. Trf. - I

L. Trf. - II

AB-II

Fatehpur Beri

V. K. ‘D’

111 MW

BTPS - I

111 MW

BTPS - II

66 MW

Bamnauli - I

66 MW

Bamnauli - II

64MW

Vasant Kunj  - I

68 MW

Vasant Kunj  - II

73 MW

100 MVA – III

220/66 KV

32 MW

IOC

ON

PALAM

45 MW

VK ‘C’-I

45 MW

VK ‘C’-II

ON

VK ‘D’-I

ON

VK ‘D’-II

30 MW

MV Ngr-I

39 MW

MV Ngr-II

22 MW

C DOT

220 KV BUS

70 MW

100 MVA – II

220/66 KV

BC

BC

11 MW

20 MVA - I

66/11 KV

66 KV BUS

11 KV BUS

Cap. Bank

77 MW

Bawana -I

87 MW

Bawana - II

39 MW

Matyala-I

Local

Transf-I

Anaj Mandi

15 MW

20 MVA -III

66/11 KV

11 MW

20 MVA - IIII

66/11 KV

70 MW

100 MVA – II

220/66 KV

70 MW

100 MVA – III

220/66 KV

70 MW

100 MVA – IV

220/66 KV

73MW

Bamnauli - I

73MW

Bamnauli - II

NJF-I

Chawla

Trunk

Rama Park

Pump Stn

Local Trf-II

Deen

Pur

DVB

Colony

TP

Kotla

Inter Conn II & III

Nagli

SPB

Kakarola

19 MW

Mtyla-II

44 MW

Bodella-I

46 MW

Bodella-II

46 MW

Nagloi

48 MW

NWW

20 MW

JfarpurI

9 MW

Jfrpur-II

Cap.

Bank

Cap. Bank

Cap.

Bank

220 KV BUS

59 MW

100 MVA – II

220/33 KV

44 MW

100 MVA – I

220/33 KV

ON

16 MVA - I

33/11 KV

BC

33 KV BUS

11 KV BUS

44 MW

BAMNAULI - I

18.5 MW

DMS

ON

Kirbi Place-II

BC

9 MW

Kirby Place-I

18 MW

Rewari Line-I

16 MW

Rewari Line-II

P. Zone

Magoo - I

KP-I

17.5 MW

116 MVA - II

33/11 KV

Gopinath

Bazar

Brar Square

KP - II

Naraina Village

MAG - II

A Block Shopping Complex

22 MW

Inder Puri

16 MW

Khyber Lane - I

6 MW

Khyber Lane - II

59MW

BAMNAULI - II

220 KV BUS

74 MW

100 MVA – II

220/66 KV

51 MW

100 MVA – III

220/66 KV

BC

3 MW

20 MVA - II

66/11 KV

42MW

J. Puri - I

15 MW

Badli-II

Capacitor

Bank

BC

41MW

J. Puri - II

66 KV BUS

11 KV BUS

Cap.

Bank

Colony

Trf.

Bawana

DSIDC

BBMB

120MW

DSIDC Bawana-I

120MW

DSIDC Bawana - II

60 MW

Panipat-I

37 MW

A 7 NARELA

37 MW

A7 NARELA

16 MW

Badli-I

7 MW

20 MVA - I

66/11 KV

77 MW

100 MVA – I

220/66 KV

DDA-5

Narela

O/H

DDA

B-4

U/G

Narela

12MW

30 MVA - I

66/33 KV

33 KV BUS

OFF

MNDL-I

OFF

MNDL-II

75 MW

Rhtk Rd-I

75 MW

Rhtk Rd-II

60 MW

Panipat-II

60 MW

Panipat-III

12MW

AIR Khampur-I

Kundli-I

ON

H. Pur-II

192 MW

BTPS - I

173 MW

BTPS - II

BC

BC

66 KV BUS

Cap Bank

5 MW

20 MVA - I

66/11 KV

19.5MW

Okhla-I

19.5MW

Okhla-II

38 MW

M. NGR-I

38 MW

M. NGR-II

316MW

TB

Cap

Bank

BC

21MW

Moth

19.5MW

Okhla PH-2-I

19 MW

Nehru Place-I

19 MW

Nehru Place-II

19 MW

T. Bad I

13.5 MW

NP III

25 MW

NP IV

OFF

EOK II

11.5 MW

EOK I

10MW

AN I

11 MW

AN II

Cap

Bank

AN

Via TA

G Ngr II

A-8

Ext

TA

G. Puri

Local Trf

DDA

LSC

G Ngr I

A-10

Ext

A-12

Ext

33 KV BUS

11 KV BUS

24 MW

50 MVA – I

220/33 KV

24 MW

50 MVA – II

220/33 KV

66MW

100 MVA – I

220/33 KV

82MW

100 MVA – II

220/33 KV

84 MW

100 MVA – I

220/66 KV

82 MW

100 MVA – II

220/66 KV

4 MW

20 MVA - II

66/11 KV

18.5MW

Okhla PH-2-II

220 KV BUS

BAMANAULI- II

82 MW

100 MVA – I

220/66 KV

78 MW

100 MVA- III

220/66 KV

13 MW

20 MVA - I

66/11 KV

BC

11 MW

20 MVA - II

66/11 KV

37 MW

B. pur-I

37 MW

B. Pur-II

66 KV BUS

11 KV BUS

Sec-II

PPK

82 MW

100 MVA – II

220/66 KV

BAMANAULI- I

45 MW

G2-II

45 MW

G2-I

25 MW

Dwarka

G6-II

Cap.

Bank

ON

Dwarka

G6-I

47 MW

Rewari Line

47 MW

Bodella-I

150 MW

170 MW

11 MW

20 MVA- III

66/11 KV

PP-I

Maha

Luxmi

Mangla

Puri

Sec-10

PPK

SEC-19

NSIT

PP-II

Bengali

Cly

Naseer

Pur

Palam Village

Ever

Green

Ninod Nagar

15 C-2

SEC-7

140 MW

Pragati-II

BC

66 KV BUS

BC

14 MW

Parsad

Nagar

14.5 MW

BR-II

18 MW

M.K.-I

23 MW

Sankar Rd.

111 MW

B.R. - I

15 MW

Faiz Road-I

33 KV BUS

83 MW

100 MVA – II

220/66 KV

62 MW

100 MVA – I

220/66 KV

34 MW

Shastri

Park-I

BC

8 MW

MK - II

10 MW

HHanuman Road

OFF

N. B.

82 MW

100 MVA – II

220/33 KV

76 MW

100 MVA – II

220/33 KV

39 MW

Shastri

Park-II

38.5 MW

Ridge

Valley-I

No Load

30 MVA- I

66/33 KV

No Load

30 MVA-II

66/33 KV

20 MW

Ridge

Valley-II

7 MW

BD Marg-I

OFF

BD Marg-II

220 KV BUS

13 MW

Faiz Road-II

158 MW

Pragati-I

15 MW

Geeta Clny - II

OFF

Sahibabad-I

BC

BC

66 KV BUS

Cap

Bank

OFF

K. Puri

COMM.

PRO.

GNC

SS-II

S. Pur

ND No. 2

NV DDA Flat

FP STRU

Preet Vihar

DVB SQ-I

R. V.

Cap.

Bank

11 KV BUS

64 MW

50 MVA – I

220/66 KV

24 MW

50 MVA – II

220/66 KV

48MW

100 MVA – I

220/33 KV

321 MW

GH-I

Cap

Bank

30 MW

V. Vihar-I

15 MW

IP Stn - I

8MW

20 MVA – I

33/11 KV

B/D

50MVA I

220/33KV

48 MW

100 MVA –I I

220/33 KV

33 KV BUS

130 MW

Geeta Clny - I

OFF

Shbabad-II

6 MW

MD

21MW

50

MVAII

220/33

KV

530 MW

V. Vihar-II

Cap

Bank

Cap.

Bank

ON

Shakarpur

15 MW

CBD

Shahadra

12MW

Karkar

Dooma I

12MW

Karkar

Dooma II

8 MW

Twin Tower

12 MW

GA Ngr-II

ON

Geeta

Colony

18 MW

GA Ngr- I

70 MW

IP Stn - II

4 MW

16 MVA – I

33/11 KV

16MW

Preet Vihar

DVB

SQ-II

ND No. I

220 KV BUS

54 MW

100 MVA – I

220/66 KV

OFF

100 MVA – II

220/66 KV

7 MW

20 MVA - I

66/11 KV

BC

6 MW

20 MVA - II

66/11 KV

66 KV BUS

11 KV BUS

54 MW

IP Extn-I

OFF

BTPS- I

17 MW

Mathura Road - I

Capacitor Bank - II

Capacitor Bank - I

OFF

IP Extn II

OFF

BTPS- II

24 MW

Mathura Road - I

220 KV BUS

35 MW

100 MVA – I

220/33 KV

22 MW

100 MVA – II

220/33 KV

OFF

20 MVA - I

33/11 KV

OFF

Civil Line - II

11 MW

BG Road-I

BC

12 MW

20 MVA - II

33/11 KV

66 KV BUS

11 KV BUS

GOPALPUR-I

GOPALPUR-II

OFF

Civil Line-I

11 MW

Gulabi Bagh

Delhi School

Kabir Basti

Parag Ice Factory

H. Rao Hosp

BG Road

Azad

Mkt.

Palace Cinema

K. K. Coll.

Subzi

Mandi

NB Cold Store

New Court

St. Stephens

Cap Bank

11 MW

Shakti Nagar

12 MW

BG Road - II

Bus PT

Spare Bay

Kamla Market

Town Hall

18MW

I. G. Stadium

STN Tx-I

Empty Way

Minto Road

Fountain

10MVAR Cap. Bank-II

G. B. Pant

31 MW

IP-II

BC

31MW

75 MVA – II

220/33 KV

12 MW

IP- I

I/C from GT-II

33 KV BUS

BC

220 KV BUS

78 MW

100 MVA- III

220/66 KV

3.5 MW

Sekhawati

B/D

100 MVA- III

220/33 KV

220 KV BUS

44 MW

100 MVA- I

220/66 KV

44 MW

100 MVA-2

220/66 KV

9 MW

20 MVA - I

66/11 KV

46 MW

Ghonda - II

16 MW

Shastri Park-I

BC

11 MW

20 MVA - II

66/11 KV

66 KV BUS

11 KV BUS

83 MW

MANDAULA-3

160 MW

G COLONY CKT-I

44MW

K.GATE

CKT-II

16MW

Shastri Park-II

45 MW

Ghonda - I

‘D’ BGE

TKMP

B-BLK

BHJNP

SV WTP-I

SV RW

SADAT PUR

31/2 P VCLNY

WBD

SW-2

MB

MNDR

SHDR BANDH

SVR

WTP-II

SVR

WTP-III

Reactor Bus Coupler

220 KV BUS

Load –67 MW

100 MVA – II

220/66 KV

BC

7 MW

20 MVA - I

66/11 KV

BC

11 MW

20 MVA - II

66/11 KV

66 KV BUS

11 KV

BUS

VK,

C-8-II

Nangal Dairy

MP Pur

AB Hot

C-9 S/S-II

V. K.

C-9

Spinal Hospital

L Trf

400 KVA

64 MW

Mehrauli - I

68 MW

Mehrauli - II

Load –65 MW

100 MVA – III

220/66 KV

12 MW

VK ‘C’-I

12 MW

VK ‘C’-II

4MW

VK ‘D’-I

5MW

VK ‘D’-II

32 MW

R.V. - I

27MW

R.V. - II

22MW

PALAM

Shunt Capacitor

Shunt Capacitor

Rang Puri

IAAI

C-8,

S/S-I

220 KV BUS

87MW MW

100 MVA – II

220/66 KV

87MW

100 MVA – I

220/66 KV

25 MW

20 MVA - I

66/11 KV

BC

66 KV BUS

11 KV BUS

Rohini 23

BC

Rohini-4-I

Rohini-5

-II

SEC-25

6/11 Rohini

DMB No. 1

No Load

20 MVA - II

66/11 KV

8/11 Rohini

480 SFS-I

NDPL Colony

Prahlad pur

DVB colony

DMB No. 2

480 SFS-II

SPS DDA

STF MCD

Rohini - SMB Circuit - I

Rohini-SMB Circuit - II

DMRC-I

Rohini 22

Rohini-

5-I

Rohini-6-II

Rohini-6-I

DMRC-II

Cap Bank

Cap Bank

Bawana -  Rohini Ckt-I

Bawana -  Rohini Ckt-II

90 MW

100 MVA – III

220/66 KV

Rohini-4-II

220 KV BUS

52 MW

100 MVA – II

220/33 KV

OFF

100 MVA – I

220/33 KV

25 MW

20 MVA - I

33/11 KV

BC

33 KV BUS

11 KV BUS

Wazirpur -I

BC

Rani Bagh-I

Rani Bagh-II

Wazirpur-III

PPR

SP Inter connect

Badli-II

No Load

16 MVA - II

33/11 KV

SBM

DISP

Prashant vihar

Badli-I

BP Sec-I

HyderpurDisp

Pitampura

11B SMB

MTD

FU Feeder

Bawana SMB Circuit - I

Bawana SMB Circuit - II

Rohini-SMB Circuit - I

Rohini-SMB Circuit - II

Haiderpur - I

SGT Nagar

SMB M. Grid

Cap-I

Cap-II

Wazirpur-IV

10 Blk SMB

Haiderpur - II

Wazirpur -II

SOW- I

ON

SOW- II

ON

Pragati Power Project

Circuit - III

13MW

U/G Jama Masjid-I

7MW

U/G Lahori Gate-II

IBT-I

STN Tx-II

7MW

U/G Jama Masjid-II

10 MVAR Cap Bank

31MW

IP-II

BC

ON

YVR - II

ON

YVR - I

42 MW

100 MVA-3

220/66 KV

NO LOAD

K. GATE

CKT-I

123 MW

G. COLONY CKT-II

170 MW

MANDAULA-4

83 MW

MANDAULA-2

97 MW

MANDAULA-I

Clear water

ON

BC

12 MW

IP- I

11.5 MW

U/G Lahori Gate-I

33 KV BUS

BC

2MW

DMRC-I

3MW

DMRC-II

5MW

100 MVA – III

220/66 KV

5 MW

Bamnauli - II

ON

Bamnauli - I

12MW

75 MVA – I

220/33 KV

220 KV BUS

66 KV BUS

220 KV BUS

ON

100 MVA – II

220/66 KV

94MW

Bay-9

I/C FROM UNIT-3

220 KV BUS

MW

SPARE

MW

Stn Tx-IV

207MW

Bay-18

I/C FROM UNIT-5

101MW

NOIDA

MW

Stn Tx-II

Stn Tx-III

25MW

BLBG-II

214MW

Bay-13

I/C FROM UNIT-4

31MW

Bay-6

I/C FROM UNIT-2

24MW

BLBG-I

60MW

SVR-II

20MW

SVR-I

MW

ALWAR

125MW

MHL-II

123 MW

MHL-I

TRANSFER BAY

186MW

OKHLA-II

184MW

OKHLA-I

MW

Stn Tx-II

Bay-II

Bay- I

BC

MW

Stn Tx-I

220 KV BUS

95MW

Bay-3

I/C FROM UNIT-1

10MW

Kilokri

54

I/C Tx-3

34

55-58

53

43-52

42

41

40

39

38

37

36

35

33

I/C Tx-I

32

31

30

29

28

27

26

25

24

23

22

21

20

19

18

17

33KV BUS

ON

Kilokri

Local

12MW

CP

Cap Bank-III

Local

ON

CP

4MW

Kilokri

7MW

Minto Road

Local

I/C of Reactor

IG Stadium-II

I/C of Reactor

9MW

CP

Stn Tx.

Cap Bank-2

5MW

Kilokri

Def. Colony

Spare

Tie Bus East

Tie Bus

West

7MW

Kamla Market-I

33KV BUS

5MW

IG Stadium

Spare

BC

10.5MW

Delhi Gate

Spare

8MW

Kamla Mkt-II

6.5MW

GB Pant

49MW

220/33kV  100MVA Tx-1

16

15

14

13

12

11

10

9

8

7

6

5

4

3

2

1

Reactor

Reactor

11.5MW

Electric Lane-II

Exh-II

Local Tx

Exh-I

10.5MW

Tilak Marg

LPN

10.5MW

N irman Bhawan-I

MW

220/33kV  100MVA Tx-3

31MW

RPH-II

13MW

RPH-I

191MW

Pragati-II

85MW

Pragati-I

33KV BUS

ON

NZM

9MW

Electric Lane-I

Inter Connector

11.5MW

Nirman Bhawaan-II

Cap Bank-I

Kilokri

42MW

220/33kV  100MVA Tx-2

BC

220 KV BUS

20MW

PPG-II

School Lane-I

BC

28MW

PPG-I

MW

100MVA Tx-I

66 KV BUS

Vidyut Bhawan-IIMW

SPARE

BC

Vidyut Bhawan-I

10MW

Narela - II

10MW

Narela - I

25MW

DMRC-II

31MW

Bay-6

I/C FROM UNIT-2

DMRC-I

20 MVA - III

66/11 KV

School Lane-II MW

ALWAR

Bay-II

Bay- I

BC

ON

100 MVA – III

220/66 KV

10 MW

Bawana - II

MW

160MVA Tx-I

220 KV BUS

94MW

Bay-9

I/C FROM UNIT-3

10MW

Bawana - I

66 KV BUS

BC

20 MVA - III

66/11 KV

BC

ON

100 MVA – II

220/66 KV

220 KV BUS