## NDPL
DELHI TRANSCO LIMITED | [15 empty] | MARCH-2012
REACTIVE ENERGY CONSUMPTION STATEMENT
Customer:NORTH DELHI POWER LIMITED.
NDPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
GOPAL PUR
1 | Tx.1 | 4864904 | ELSTER | Kvarh(Lead/Lag) | -1000 | 16112 | 16988 | -876 | 876000 | 0.876 | 978429 | 978429 | 0 | 0 | 0
2 | TX.2 | 5128432 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1000014 | 999628 | 386 | -386000 | -0.386 | 52 | 87 | -35 | 35000 | 0.035 | ROLL OVER
3 | Tx.3 | 4864905 | ELSTER | Kvarh(Lead/Lag) | -1000 | 17297 | 18022 | -725 | 725000 | 0.725 | 997175 | 997175 | 0 | 0 | 0
SUBZI MANDI
4 | Tx.1 | 4864912 | ELSTER | Kvarh(Lead/Lag) | -1000 | 974212 | 974388 | -176 | 176000 | 0.176 | 978291 | 978394 | -103 | 103000 | 0.103
5 | Tx.2 | 4864913 | ELSTER | Kvarh(Lead/Lag) | -1000 | 922019 | 922401 | -382 | 382000 | 0.382 | 949919 | 949919 | 0 | 0 | 0
ROHINI
6 | Tx.1 | 4864982 | ELSTER | Kvarh(Lead/Lag) | -1000 | 18707 | 18736 | -29 | 29000 | 0.029 | 16555 | 16661 | -106 | 106000 | 0.106
7 | Tx.2 | 4864983 | ELSTER | Kvarh(Lead/Lag) | -1000 | 19625 | 19677 | -52 | 52000 | 0.052 | 12677 | 12778 | -101 | 101000 | 0.101
8 | Tx.-3 | 4864953 | ELSTER | Kvarh(Lead/Lag) | -1000 | 17076 | 17076 | 0 | 0 | 0 | 996633 | 996633 | 0 | 0 | 0 | YCT Changes from800/1 to 1000/1 on dated 21/03/12
8 | Tx.-3 | 4864953 | ELSTER | Kvarh(Lead/Lag) | -1250 | 16953 | 17076 | -123 | 153750 | 0.15375 | 996631 | 996633 | -2 | 2500 | 0.0025
9 | Tx.-4 | 4864984 | ELSTER | Kvarh(Lead/Lag) | -1000 | 15956 | 16414 | -458 | 458000 | 0.458 | 986832 | 986837 | -5 | 5000 | 0.005
SHALIMAR BAGH
10 | Tx.1 | 4864939 | ELSTER | Kvarh(Lead/Lag) | -1000 | 33999 | 34633 | -634 | 634000 | 0.634 | 9808 | 9828 | -20 | 20000 | 0.02
11 | Tx.-2 | 4864940 | ELSTER | Kvarh(Lead/Lag) | -1000 | 669 | 1454 | -785 | 785000 | 0.785 | 4167 | 4179 | -12 | 12000 | 0.012
12 | Tx.-3 | 5128410 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997883 | 998246 | -363 | 363000 | 0.363 | 999513 | 999514 | -1 | 1000 | 0.001
13 | 220KV DMRC | 4865060 | ELSTER | Kvarh(Lead/Lag) | 1000 | 950702 | 952721 | -2019 | -2019000 | -2.019 | 920550 | 920550 | 0 | 0 | 0
NARELA
14 | Tx.1 | 4865034 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997244 | 997361 | -117 | 117000 | 0.117 | 17149 | 17155 | -6 | 6000 | 0.006
15 | Tx.2 | 4865035 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999634 | 999531 | 103 | -103000 | -0.103 | 19555 | 19558 | -3 | 3000 | 0.003
16 | Tx.3 | 4902500 | ELSTER | Kvarh(Lead/Lag) | -1000 | 782 | 872 | -90 | 90000 | 0.09 | 21005 | 21027 | -22 | 22000 | 0.022
NARAINA
17 | O/G REWARI LINE 1 | 4864886 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999546 | 999546 | 0 | 0 | 0 | 28203 | 28111 | 92 | 92000 | 0.092
18 | O/G REWARI LINE 2 | 4864887 | ELSTER | Kvarh(Lead/Lag) | 1000 | 212 | 209 | 3 | 3000 | 0.003 | 26660 | 26569 | 91 | 91000 | 0.091
19 | 16 MVA TX.-1 | 4864798 | ELSTER | Kvarh(Lead/Lag) | 100 | 2306 | 2183 | 123 | 12300 | 0.0123 | 123207 | 122668 | 539 | 53900 | 0.0539
20 | 16 MVA TX.-2 | 4864799 | ELSTER | Kvarh(Lead/Lag) | 100 | 4109 | 3846 | 263 | 26300 | 0.0263 | 172420 | 171592 | 828 | 82800 | 0.0828
21 | INDER PURI | 4864888 | ELSTER | Kvarh(Lead/Lag) | 1000 | 996023 | 996034 | -11 | -11000 | -0.011 | 997585 | 997594 | -9 | -9000 | -0.009
22 | INDER PURI-2 | 5128402 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999909 | 999916 | -7 | -7000 | -0.007 | 1804 | 1776 | 28 | 28000 | 0.028
KASHMIRI GATE
23 | 221 kV DMRC #1 | 4865057 | ELSTER | Kvarh(Lead/Lag) | 1000 | 652985 | 653600 | -615 | -615000 | -0.615 | 801377 | 801382 | -5 | -5000 | -0.005
24 | 221 kV DMRC #2 | 4865058 | ELSTER | Kvarh(Lead/Lag) | 1000 | 659982 | 660261 | -279 | -279000 | -0.279 | 833849 | 833850 | -1 | -1000 | -0.001
25 | CIVIL LINE | 4864889 | ELSTER | Kvarh(Lead/Lag) | 1000 | 991489 | 991381 | 108 | 108000 | 0.108 | 998460 | 998460 | 0 | 0 | 0
26 | CIVIL LINE-2 | 5128405 | ELSTER | Kvarh(Lead/Lag) | 500 | 1000006 | 999877 | 129 | 64500 | 0.0645 | 999843 | 999839 | 4 | 2000 | 0.002 | ROLL OVER
KANJAWALA
27 | TX-1 | 4865054 | ELSTER | Kvarh(Lead/Lag) | -1000 | 8057 | 7897 | 160 | -160000 | -0.16 | 981904 | 981899 | 5 | -5000 | -0.005
28 | Tx.2 | 4865055 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1000059 | 999512 | 547 | -547000 | -0.547 | 948563 | 948565 | -2 | 2000 | 0.002 | ROLL OVER
BAWANA
29 | I/C 100 MVA PR.TR. | 4865056 | ELSTER | Kvarh(Lead/Lag) | -1000 | 991761 | 991885 | -124 | 124000 | 0.124 | 933409 | 933543 | -134 | 134000 | 0.134
DSIDC BAWANA
30 | 66KV TX.2 | 4865049 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999834 | 1000141 | -307 | 307000 | 0.307 | 0 | 0 | 0 | 0 | 0 | ROLL OVER
31 | 66KV TX.3 | 4865022 | ELSTER | Kvarh(Lead/Lag) | -1000 | 9985 | 7876 | 2109 | -2109000 | -2.109 | 999970 | 999977 | -7 | 7000 | 0.007
EXPORT TO EAST & CENTRE IMPORTS
SHASTRI PARK
32 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | 1000 | 687 | 701 | -14 | -14000 | -0.014 | 16372 | 16325 | 47 | 47000 | 0.047
33 | PUSA GRID-II | 4864844 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999419 | 999317 | 102 | 102000 | 0.102 | 3175 | 3073 | 102 | 102000 | 0.102
| NDPL(+) continue | [14 empty] | MARCH-2012
DMS
34 | 33KV PANDAV NGR | 4865169 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1286 | 1144 | 142 | 142000 | 0.142 | 56251 | 56115 | 136 | 136000 | 0.136
REWARI LINE
35 | 20MVA Tx-2 | 4864824 | ELSTER | Kvarh(Lead/Lag) | 100 | 14018 | 12630 | 1388 | 138800 | 0.1388 | 61784 | 61758 | 26 | 2600 | 0.0026
VISHAL
36 | RAMESH NAGAR-1 | 4865090 | ELSTER | Kvarh(Lead/Lag) | 100 | 8781 | 8429 | 352 | 35200 | 0.0352 | 13976 | 13734 | 242 | 24200 | 0.0242
37 | BALI NAGAR -1 | 4902519 | ELSTER | Kvarh(Lead/Lag) | 100 | 9668 | 9595 | 73 | 7300 | 0.0073 | 30964 | 30919 | 45 | 4500 | 0.0045
38 | ESI HOSPITAL | 4902520 | ELSTER | Kvarh(Lead/Lag) | 100 | 13752 | 13736 | 16 | 1600 | 0.0016 | 38042 | 37334 | 708 | 70800 | 0.0708
S.B.MILL
39 | MOTI NAGAR KIOSK | 4902521 | ELSTER | Kvarh(Lead/Lag) | 100 | 33100 | 32745 | 355 | 35500 | 0.0355 | 10957 | 10896 | 61 | 6100 | 0.0061
40 | 53 RAMA ROAD | 4902522 | ELSTER | Kvarh(Lead/Lag) | 100 | 840 | 840 | 0 | 0 | 0 | 185 | 185 | 0 | 0 | 0
41 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | 100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
42 | 70 RAMA ROAD | 4902524 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | MOTI NAGAR 2 | 4902525 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | NAJAFGARH ROAD | 4902526 | ELSTER | Kvarh(Lead/Lag) | 100 | 15843 | 15724 | 119 | 11900 | 0.0119 | 11244 | 11217 | 27 | 2700 | 0.0027
45 | PHILIPS | 4902527 | ELSTER | Kvarh(Lead/Lag) | 100 | 997311 | 997513 | -202 | -20200 | -0.0202 | 1324 | 1313 | 11 | 1100 | 0.0011
B.G.ROAD
46 | CSA | 4865091 | ELSTER | Kvarh(Lead/Lag) | 500 | 5126 | 5110 | 16 | 8000 | 0.008 | 22836 | 22767 | 69 | 34500 | 0.0345
47 | DCM NO.1 | 4902530 | ELSTER | Kvarh(Lead/Lag) | 500 | 3309 | 3290 | 19 | 9500 | 0.0095 | 20845 | 20803 | 42 | 21000 | 0.021
48 | DCM NO.2 | 4902531 | ELSTER | Kvarh(Lead/Lag) | 500 | 3333 | 3296 | 37 | 18500 | 0.0185 | 13991 | 13973 | 18 | 9000 | 0.009
49 | SADAR S/S | 4902532 | ELSTER | Kvarh(Lead/Lag) | 500 | 3282 | 3237 | 45 | 22500 | 0.0225 | 16355 | 16305 | 50 | 25000 | 0.025
D.M.S.
50 | PHILIPS | 4902535 | ELSTER | Kvarh(Lead/Lag) | 100 | 999173 | 999458 | -285 | -28500 | -0.0285 | 5799 | 5798 | 1 | 100 | 0.0001
51 | 69 NG ROAD | 4902536 | ELSTER | Kvarh(Lead/Lag) | 100 | 3431 | 3199 | 232 | 23200 | 0.0232 | 13740 | 13730 | 10 | 1000 | 0.001
52 | J BLOCK KIRTI NGR | 4902537 | ELSTER | Kvarh(Lead/Lag) | 100 | 8850 | 8229 | 621 | 62100 | 0.0621 | 48869 | 48858 | 11 | 1100 | 0.0011
53 | H BLOCK | 4902538 | ELSTER | Kvarh(Lead/Lag) | 100 | 8005 | 8020 | -15 | -1500 | -0.0015 | 19046 | 19056 | -10 | -1000 | -0.001
54 | SHADI KHAM PUR | 4902539 | ELSTER | Kvarh(Lead/Lag) | 100 | 999421 | 999469 | -48 | -4800 | -0.0048 | 251 | 251 | 0 | 0 | 0
55 | BREAK FAST | 4902540 | ELSTER | Kvarh(Lead/Lag) | 100 | 15 | 15 | 0 | 0 | 0 | 13398 | 13398 | 0 | 0 | 0
FAIZ ROAD
56 | TIBIA COLLEGE-1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | 100 | 3289 | 3000 | 289 | 28900 | 0.0289 | 62857 | 62470 | 387 | 38700 | 0.0387
57 | TIBIA COLLEGE-2 | 4902542 | ELSTER | Kvarh(Lead/Lag) | 100 | 5026 | 4747 | 279 | 27900 | 0.0279 | 53456 | 53276 | 180 | 18000 | 0.018
58 | MANAK PURA | 4902543 | ELSTER | Kvarh(Lead/Lag) | 100 | 5889 | 5520 | 369 | 36900 | 0.0369 | 77456 | 77069 | 387 | 38700 | 0.0387
KASHMIRI GATE
59 | 20MVA TX. | 4864807 | ELSTER | Kvarh(Lead/Lag) | 100 | 113953 | 112336 | 1617 | 161700 | 0.1617 | 27008 | 27000 | 8 | 800 | 0.0008
60 | FLYOVER | 4865086 | ELSTER | Kvarh(Lead/Lag) | 100 | 16028 | 15602 | 426 | 42600 | 0.0426 | 33515 | 33512 | 3 | 300 | 0.0003
61 | B/C (IMP. TO NDPL) | 4902571 | ELSTER | Kvarh(Lead/Lag) | -300 | 41 | 41 | 0 | 0 | 0 | 23 | 23 | 0 | 0 | 0
REWARI LINE (11KV TRANSFER OF ENERGY)
62 | BSES -NDPL(EX.) ON BUS-1&2 | 4865087 | ELSTER | Kvarh(Lead/Lag) | -400 | 4570 | 4570 | 0 | 0 | 0 | 12611 | 12610 | 1 | -400 | -0.0004
63 | BSES -NDPL(EX.) ON BUS-2&3 | 4902516 | ELSTER | Kvarh(Lead/Lag) | 100 | 999301 | 999305 | -4 | -400 | -0.0004 | 999393 | 999274 | 119 | 11900 | 0.0119
Mundka
64 | 66KV MANGOL PURI | 5128444 | ELSTER | Kvarh(Lead/Lag) | 800 | 999840 | 999791 | 49 | 39200 | 0.0392 | 0 | 0 | 0 | 0 | 0
| ENERGY INPUT AT 66/33/11 KV LEVEL | [8 empty] | 0.13575 |  |  |  |  | 1.4849
NDPL(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 % |  |  | MARCH-2012
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
NARAINA
1 | GOPI NATH BAZAAR | 4865092 | ELSTER | Kvarh(Lead/Lag) | -100 | 6548 | 6347 | 201 | -20100 | -0.0201 | 9442 | 9245 | 197 | -19700 | -0.0197
MANGOLPURI
2 | NANGLOI-2 EXP | 4864955 | ELSTER | Kvarh(Lead/Lag) | -1000 | 6003 | 5818 | 185 | -185000 | -0.185 | 4633 | 4522 | 111 | -111000 | -0.111
SUBZI MANDI
3 | O/G BG Rd.1 | 4864808 | ELSTER | Kvarh(Lead/Lag) | -200 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 | O/G BG Rd.2 | 4864841 | ELSTER | Kvarh(Lead/Lag) | -1000 | 13301 | 13198 | 103 | -103000 | -0.103 | 24730 | 24687 | 43 | -43000 | -0.043
SUDARSHAN PARK
5 | VISHAL (EXP) | 4864792 | ELSTER | Kvarh(Lead/Lag) | -100 | 38246 | 38725 | -479 | 47900 | 0.0479 | 147056 | 147054 | 2 | -200 | -0.0002
REWARI LINE (ENERGY EXCHANGE WITH NDPL)
6 | 33KV B/C | 4865170 | ELSTER | Kvarh(Lead/Lag) | -1000 | 0 | 0 | 0 | 0 | 0 | 999972 | 999972 | 0 | 0 | 0
KANJAWALA
7 | 66KV DMRC | 4864961 | ELSTER | Kvarh(Lead/Lag) | -1000 | 974433 | 975361 | -928 | 928000 | 0.928 | 992679 | 992681 | -2 | 2000 | 0.002
MUNDKA
8 | 66KV NGL. T-OFF MGL P | 5128407 | ELSTER | Kvarh(Lead/Lag) | 2000 | 999898 | 999933 | -35 | -70000 | -0.07 | 0 | 0 | 0 | 0 | 0
| TOTAL OF INTER COMPANY EXCHANGE POINTS | [8 empty] | 0.5978 |  |  |  |  | -0.1719
EXECUTIVE SUMMERY N.D.P.L.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (Refer sheet NDPL(+)) | [9 empty] | 0.13575 |  |  |  |  | 1.4849
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet NDPL(-)) | [9 empty] | 0.5978 |  |  |  |  | -0.1719
3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL) | [9 empty] | 2.0721 |  |  |  |  | 0.061288
NET ENERGY TO NORTH DELHI POWER LIMITED | [9 empty] | 2.8057 |  |  |  |  | 1.3743
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 2.8057 | (REACTIVE MUs) |  |  |  | 1.3743 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.094092 | (REACTIVE MUs) |  |  |  | 1.6859 | (REACTIVE MUs)
[9 empty] | TOTAL | 2.7116 | (REACTIVE MUs) |  |  |  | 3.0602 | (REACTIVE MUs)

## BYPL
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [15 empty] | MARCH-2012
Customer:BSES YAMUNA POWER LIMITED.
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION 33KV FEEDER
1 | KAMLA MKT.-B-18 | 4865098 | ELSTER | Kvarh(Lead/Lag) | 100 | 999998 | 999998 | 0 | 0 | 0 | 37954 | 37954 | 0 | 0 | 0
2 | KAMLA MKT.B-30 | 4865161 | ELSTER | Kvarh(Lead/Lag) | 100 | 988780 | 988822 | -42 | -4200 | -0.0042 | 79117 | 75483 | 3634 | 363400 | 0.3634
3 | P. HOSPITAL BAY-19 | 4865099 | ELSTER | Kvarh(Lead/Lag) | 100 | 17233 | 17284 | -51 | -5100 | -0.0051 | 1305 | 1085 | 220 | 22000 | 0.022
4 | IG STD- BAY-29 | 4865162 | ELSTER | Kvarh(Lead/Lag) | 100 | 23872 | 23923 | -51 | -5100 | -0.0051 | 31018 | 30857 | 161 | 16100 | 0.0161
5 | IG STD-BAY 31 | 4865100 | ELSTER | Kvarh(Lead/Lag) | 100 | 998853 | 998866 | -13 | -1300 | -0.0013 | 7643 | 7256 | 387 | 38700 | 0.0387
6 | DELHI GATE B-17 | 4865101 | ELSTER | Kvarh(Lead/Lag) | 100 | 8839 | 8842 | -3 | -300 | -0.0003 | 77717 | 77411 | 306 | 30600 | 0.0306
7 | MINTO RD. B-34 | 4865102 | ELSTER | Kvarh(Lead/Lag) | 100 | 550 | 715 | -165 | -16500 | -0.0165 | 48547 | 48476 | 71 | 7100 | 0.0071
RPH
8 | KAMLA MKT.-2 | 4864884 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999615 | 999616 | -1 | -1000 | -0.001 | 999775 | 999774 | 1 | 1000 | 0.001
9 | FOUNTAIN BAY-16 | 4864831 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999797 | 999807 | -10 | -10000 | -0.01 | 2282 | 2273 | 9 | 9000 | 0.009
10 | MINTO RD BAY-17 | 4864832 | ELSTER | Kvarh(Lead/Lag) | 1000 | 406 | 408 | -2 | -2000 | -0.002 | 1692 | 1545 | 147 | 147000 | 0.147
11 | TOWN HALL-3 | 4864833 | ELSTER | Kvarh(Lead/Lag) | 1000 | 91 | 84 | 7 | 7000 | 0.007 | 3278 | 2755 | 523 | 523000 | 0.523
12 | LAHORI GATE-1 | 4864834 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999726 | 999742 | -16 | -16000 | -0.016 | 2575 | 2436 | 139 | 139000 | 0.139
13 | LAHORI GATE-2 | 4864835 | ELSTER | Kvarh(Lead/Lag) | 1000 | 449 | 455 | -6 | -6000 | -0.006 | 1099 | 1060 | 39 | 39000 | 0.039
14 | JAMA MASJID-1 | 4864836 | ELSTER | Kvarh(Lead/Lag) | 1000 | 155 | 158 | -3 | -3000 | -0.003 | 14816 | 14262 | 554 | 554000 | 0.554
15 | JAMA MASJID-2 | 4864837 | ELSTER | Kvarh(Lead/Lag) | 1000 | 293 | 299 | -6 | -6000 | -0.006 | 34702 | 34443 | 259 | 259000 | 0.259
16 | GB PANTH(Bay-13) | 4864838 | ELSTER | Kvarh(Lead/Lag) | 1000 | 255 | 254 | 1 | 1000 | 0.001 | 12010 | 11355 | 655 | 655000 | 0.655
17 | SACHV. (Bay-12) | 4864839 | ELSTER | Kvarh(Lead/Lag) | 1000 | 252 | 246 | 6 | 6000 | 0.006 | 5518 | 5411 | 107 | 107000 | 0.107
18 | 6.6 KV IRRG.PUMP | 4864786 | ELSTER | Kvarh(Lead/Lag) | 100 | 32134 | 31830 | 304 | 30400 | 0.0304 | 536 | 536 | 0 | 0 | 0
19 | KAMLA MKT. (B-19) | 4864883 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998541 | 998550 | -9 | -9000 | -0.009 | 8251 | 6753 | 1498 | 1498000 | 1.498
GT
20 | DMRC. CKT.-I | 4865041 | ELSTER | Kvarh(Lead/Lag) | 1100 | 999998 | 999998 | 0 | 0 | 0 | 822999 | 826115 | -3116 | -3427600 | -3.4276
21 | DMRC CKT.-II | 4865042 | ELSTER | Kvarh(Lead/Lag) | 1100 | 999999 | 999999 | 0 | 0 | 0 | 865087 | 868117 | -3030 | -3333000 | -3.333
22 | AKSHARDHAM | 4864943 | ELSTER | Kvarh(Lead/Lag) | 1000 | 992552 | 992757 | -205 | -205000 | -0.205 | 10042 | 10042 | 0 | 0 | 0
| KASHMIRI GATE | [8 empty] | -0.2136 |  |  |  |  | -2.8296
23 | 100 MVA TX.-1 | 4864910 | ELSTER | Kvarh(Lead/Lag) | -1000 | 965064 | 965264 | -200 | 200000 | 0.2 | 977930 | 977952 | -22 | 22000 | 0.022
24 | 100 MVA TX.-2 | 4864911 | ELSTER | Kvarh(Lead/Lag) | -1000 | 981351 | 981843 | -492 | 492000 | 0.492 | 984020 | 984034 | -14 | 14000 | 0.014
25 | B/C (IMP. TO BYPL) | 4902571 | ELSTER | Kvarh(Lead/Lag) | 300 | 41 | 41 | 0 | 0 | 0 | 23 | 23 | 0 | 0 | 0
NARAINA
26 | DMS | 4864830 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1212 | 1149 | 63 | 63000 | 0.063 | 57497 | 57209 | 288 | 288000 | 0.288
PARK STREET
27 | TX.-1 (66KV) | 4864962 | ELSTER | Kvarh(Lead/Lag) | -1000 | 8535 | 5981 | 2554 | -2554000 | -2.554 | 974685 | 974704 | -19 | 19000 | 0.019
28 | TX.-2(66KV) | 4865033 | ELSTER | Kvarh(Lead/Lag) | -1000 | 7024 | 6352 | 672 | -672000 | -0.672 | 977630 | 978443 | -813 | 813000 | 0.813
29 | TX.-1(33KV) | 4864902 | ELSTER | Kvarh(Lead/Lag) | -1000 | 991512 | 992962 | -1450 | 1450000 | 1.45 | 990807 | 990908 | -101 | 101000 | 0.101
30 | TX.-2(33KV) | 4864935 | ELSTER | Kvarh(Lead/Lag) | -1000 | 992603 | 994773 | -2170 | 2170000 | 2.17 | 995905 | 995989 | -84 | 84000 | 0.084
IMPORTS
SUBZI MANDI
31 | O/G BG Rd.1 | 4864808 | ELSTER | Kvarh(Lead/Lag) | 200 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
32 | O/G BG Rd.2 | 4864841 | ELSTER | Kvarh(Lead/Lag) | 1000 | 13301 | 13198 | 103 | 103000 | 0.103 | 24730 | 24687 | 43 | 43000 | 0.043
RIDGE VALLEY
33 | O/G SHANKAR RD.1 | 4865134 | ELSTER | Kvarh(Lead/Lag) | 100 | 91786 | 92317 | -531 | -53100 | -0.0531 | 1707 | 1707 | 0 | 0 | 0
34 | O/G SHANKAR RD.2 | 4865135 | ELSTER | Kvarh(Lead/Lag) | 100 | 59899 | 54266 | 5633 | 563300 | 0.5633 | 999577 | 999577 | 0 | 0 | 0
| ENERGY INPUT AT 66/33KK LEVEL | [8 empty] | 1.5161 |  |  |  |  | -0.9677
| (A) NET ENERGY TO CENTRAL | [8 empty] | 1.5161 |  |  |  |  | -0.9677
MARCH-2012
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
S.O.W.
1 | Tx.1 | 4864968 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996842 | 997090 | -248 | 248000 | 0.248 | 939658 | 940297 | -639 | 639000 | 0.639
2 | Tx.2 | 4864980 | ELSTER | Kvarh(Lead/Lag) | -1000 | 15157 | 15321 | -164 | 164000 | 0.164 | 958045 | 958734 | -689 | 689000 | 0.689
3 | Tx.3 | 4864981 | ELSTER | Kvarh(Lead/Lag) | -1000 | 12952 | 13264 | -312 | 312000 | 0.312 | 945944 | 946538 | -594 | 594000 | 0.594
PPG
4 | Tx.1 (66 KV) | 4864915 | ELSTER | Kvarh(Lead/Lag) | -1000 | 950408 | 952874 | -2466 | 2466000 | 2.466 | 993727 | 993729 | -2 | 2000 | 0.002
5 | Tx.2 (66 KV) | 4864993 | ELSTER | Kvarh(Lead/Lag) | -1000 | 940981 | 943653 | -2672 | 2672000 | 2.672 | 992018 | 992020 | -2 | 2000 | 0.002
6 | 100 MVA Tx.1 (33 KV) | 4864914 | ELSTER | Kvarh(Lead/Lag) | -1000 | 83 | 21 | 62 | -62000 | -0.062 | 993445 | 993735 | -290 | 290000 | 0.29
7 | 50 MVA Tx.-2 (33 KV) | 4865167 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1670 | 1669 | 1 | -1000 | -0.001 | 983387 | 983574 | -187 | 187000 | 0.187
8 | 50MVA Tx.3 (33 KV) | 4864893 | ELSTER | Kvarh(Lead/Lag) | -2000 | 998670 | 998741 | -71 | 142000 | 0.142 | 989707 | 989967 | -260 | 520000 | 0.52
9 | 100MVA Tx.4 (33 KV) | 4864918 | ELSTER | Kvarh(Lead/Lag) | -1000 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
GEETA COLONY
10 | I/C-I | 4864916 | ELSTER | Kvarh(Lead/Lag) | -1000 | 12444 | 12498 | -54 | 54000 | 0.054 | 956728 | 956837 | -109 | 109000 | 0.109
11 | I/C-II | 4864917 | ELSTER | Kvarh(Lead/Lag) | -1000 | 966277 | 966754 | -477 | 477000 | 0.477 | 899153 | 900587 | -1434 | 1434000 | 1.434
GAZIPUR
12 | TX.-1 | 4865053 | ELSTER | Kvarh(Lead/Lag) | -1000 | 21379 | 21368 | 11 | -11000 | -0.011 | 29504 | 28992 | 512 | -512000 | -0.512
13 | TX-2 | 4864986 | ELSTER | Kvarh(Lead/Lag) | -1000 | 19257 | 19203 | 54 | -54000 | -0.054 | 36631 | 36544 | 87 | -87000 | -0.087
SB MILL
14 | ZAKHIRA | 4902528 | ELSTER | Kvarh(Lead/Lag) | 100 | 11525 | 11525 | 0 | 0 | 0 | 4086 | 4086 | 0 | 0 | 0
| ENERGY INPUT AT 66/33/11KV LEVEL | [8 empty] | 6.407 |  |  |  |  | 3.867
| (B) NET ENERGY TO EAST | [8 empty] | 6.407 |  |  |  |  | 3.867
6
MARCH-2012
BYPL(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
KASHMIRI GATE
1 | CIVIL LINE | 4864889 | ELSTER | Kvarh(Lead/Lag) | -1000 | 991489 | 991381 | 108 | -108000 | -0.108 | 998460 | 998460 | 0 | 0 | 0
2 | CIVIL LINE-2 | 5128405 | ELSTER | Kvarh(Lead/Lag) | -500 | 1000006 | 999877 | 129 | -64500 | -0.0645 | 999843 | 999839 | 4 | -2000 | -0.002 | ROLL OVER
EXPORT TO NDMC FROM PARK STREET
3 | BAIRD RD.1 | 4865136 | ELSTER | Kvarh(Lead/Lag) | -200 | 24406 | 22606 | 1800 | -360000 | -0.36 | 62490 | 62452 | 38 | -7600 | -0.0076
4 | BAIRD RD.2 | 4865137 | ELSTER | Kvarh(Lead/Lag) | -100 | 38195 | 32631 | 5564 | -556400 | -0.5564 | 121505 | 121413 | 92 | -9200 | -0.0092
5 | NIRMAN BHAWAN | 4865138 | ELSTER | Kvarh(Lead/Lag) | -200 | 988843 | 989526 | -683 | 136600 | 0.1366 | 4293 | 4264 | 29 | -5800 | -0.0058
6 | H.LANE | 4865139 | ELSTER | Kvarh(Lead/Lag) | -200 | 44652 | 42190 | 2462 | -492400 | -0.4924 | 80321 | 80276 | 45 | -9000 | -0.009
7 | 66 KV BD MARG-I | 4864948 | ELSTER | Kvarh(Lead/Lag) | -1000 | 67410 | 67669 | -259 | 259000 | 0.259 | 232 | 232 | 0 | 0 | 0
8 | 66 KV BD MARG-II | 4864949 | ELSTER | Kvarh(Lead/Lag) | -1000 | 5877 | 3498 | 2379 | -2379000 | -2.379 | 54 | 54 | 0 | 0 | 0
9 | 66KV DMRC | 5128434 | ELSTER | Kvarh(Lead/Lag) | -800 | 994597 | 996079 | -1482 | 1185600 | 1.1856 | 998394 | 998437 | -43 | 34400 | 0.0344
10 | 66KV GUEST HOUSE | 5128445 | ELSTER | Kvarh(Lead/Lag) | -800 | 2398 | 1132 | 1266 | -1012800 | -1.0128 | 160 | 126 | 34 | -27200 | -0.0272
EXPORT TO SOUTH & WEST FROM PARK STREET
11 | 66KV R VALLEY-1 | 4864951 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997432 | 998045 | -613 | 613000 | 0.613 | 38056 | 38077 | -21 | 21000 | 0.021
12 | 66KV R VALLEY-2 | 4902501 | ELSTER | Kvarh(Lead/Lag) | -1333.33 | 997353 | 997835 | -482 | 642665.06 | 0.64267 | 491 | 499 | -8 | 10666.64 | 0.010667
EXPORT TO NORTH from SHASTRI PARK
13 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | -1000 | 687 | 701 | -14 | 14000 | 0.014 | 16372 | 16325 | 47 | -47000 | -0.047
14 | PUSA GRID-II | 4864844 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999419 | 999317 | 102 | -102000 | -0.102 | 3175 | 3073 | 102 | -102000 | -0.102
DMS
15 | 33KV PANDAV NGR | 4865169 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1286 | 1144 | 142 | -142000 | -0.142 | 56251 | 56115 | 136 | -136000 | -0.136
EXCHANGE OF ENERGY 11KV
EXPORTS
B.G.ROAD
16 | CSA | 4865091 | ELSTER | Kvarh(Lead/Lag) | -500 | 5126 | 5110 | 16 | -8000 | -0.008 | 22836 | 22767 | 69 | -34500 | -0.0345
17 | DCM NO.1 | 4902530 | ELSTER | Kvarh(Lead/Lag) | -500 | 3309 | 3290 | 19 | -9500 | -0.0095 | 20845 | 20803 | 42 | -21000 | -0.021
18 | DCM NO.2 | 4902531 | ELSTER | Kvarh(Lead/Lag) | -500 | 3333 | 3296 | 37 | -18500 | -0.0185 | 13991 | 13973 | 18 | -9000 | -0.009
19 | SADAR S/S | 4902532 | ELSTER | Kvarh(Lead/Lag) | -500 | 3282 | 3237 | 45 | -22500 | -0.0225 | 16355 | 16305 | 50 | -25000 | -0.025
KASHMIRI GATE
20 | 20MVA TX. | 4864807 | ELSTER | Kvarh(Lead/Lag) | -100 | 113953 | 112336 | 1617 | -161700 | -0.1617 | 27008 | 27000 | 8 | -800 | -0.0008
21 | FLY OVER | 4865086 | ELSTER | Kvarh(Lead/Lag) | -100 | 16028 | 15602 | 426 | -42600 | -0.0426 | 33515 | 33512 | 3 | -300 | -0.0003
D.M.S.
22 | PHILIPS | 4902535 | ELSTER | Kvarh(Lead/Lag) | -100 | 999173 | 999458 | -285 | 28500 | 0.0285 | 5799 | 5798 | 1 | -100 | -0.0001
23 | 69 NG ROAD | 4902536 | ELSTER | Kvarh(Lead/Lag) | -100 | 3431 | 3199 | 232 | -23200 | -0.0232 | 13740 | 13730 | 10 | -1000 | -0.001
24 | J BLOCK KIRTI NGR | 4902537 | ELSTER | Kvarh(Lead/Lag) | -100 | 8850 | 8229 | 621 | -62100 | -0.0621 | 48869 | 48858 | 11 | -1100 | -0.0011
25 | H BLOCK | 4902538 | ELSTER | Kvarh(Lead/Lag) | -100 | 8005 | 8020 | -15 | 1500 | 0.0015 | 19046 | 19056 | -10 | 1000 | 0.001
26 | SHADI KHAM PUR | 4902539 | ELSTER | Kvarh(Lead/Lag) | -100 | 999421 | 999469 | -48 | 4800 | 0.0048 | 251 | 251 | 0 | 0 | 0
27 | BREAK FAST | 4902540 | ELSTER | Kvarh(Lead/Lag) | -100 | 15 | 15 | 0 | 0 | 0 | 13398 | 13398 | 0 | 0 | 0
FAIZ ROAD
28 | TIBIA COLLEGE-1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | -100 | 3289 | 3000 | 289 | -28900 | -0.0289 | 62857 | 62470 | 387 | -38700 | -0.0387
29 | TIBIA COLLEGE-2 | 4902542 | ELSTER | Kvarh(Lead/Lag) | -100 | 5026 | 4747 | 279 | -27900 | -0.0279 | 53456 | 53276 | 180 | -18000 | -0.018
30 | MANAK PURA | 4902543 | ELSTER | Kvarh(Lead/Lag) | -100 | 5889 | 5520 | 369 | -36900 | -0.0369 | 77456 | 77069 | 387 | -38700 | -0.0387
[10 empty] | -2.7732 |  |  |  |  | -0.46693
MARCH-2012
EXECUTIVE SUMMARY
ENERGY RELEASED TO CENTRAL
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre A- Page -1) | [8 empty] | 1.5161 |  |  |  |  | -0.9677
| 2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer C Page-3) | [8 empty] | -2.7732 |  |  |  |  | -0.46693
| 3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL.) | [8 empty] | -1.2973 |  |  |  |  | -0.0013
| TOTAL ENERGY TO BSES YAMUNA POWER LTD. - CENTRAL PART | [8 empty] | -2.5544 |  |  |  |  | -1.4359
ENERGY RELEASED TO EAST
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre B- Page -2) | [8 empty] | 6.407 |  |  |  |  | 3.867
| NET ENERGY TO BSES YAMUNA POWER LIMITED | [8 empty] | 3.8526 |  |  |  |  | 2.4311
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 3.8526 | (REACTIVE MUs) |  |  |  | 2.4311 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.07779 | (REACTIVE MUs) |  |  |  | 1.3938 | (REACTIVE MUs)
[9 empty] | TOTAL | 3.7748 | (REACTIVE MUs) |  |  |  | 3.8248 | (REACTIVE MUs)

## BRPL
DELHI TRANSCO LIMITED | [14 empty] | MARCH-2012
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-BSES RAJDHANI POWER LIMITED
BRPL (+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION
1 | BAY-24 | 4865180 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998234 | 998319 | -85 | -85000 | -0.085 | 11010 | 11091 | -81 | -81000 | -0.081
2 | BAY-25 | 4865095 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 990541 | 990605 | -64 | -85333.12 | -0.085333 | 677598 | 677610 | -12 | -15999.96 | -0.016
3 | BAY-13 | 4865166 | ELSTER | Kvarh(Lead/Lag) | 1000 | 6677 | 6623 | 54 | 54000 | 0.054 | 47101 | 46355 | 746 | 746000 | 0.746
4 | BAY-53 | 4865151 | ELSTER | Kvarh(Lead/Lag) | 1000 | 10896 | 10881 | 15 | 15000 | 0.015 | 874 | 698 | 176 | 176000 | 0.176
5 | BAY-54 | 4865152 | ELSTER | Kvarh(Lead/Lag) | 300 | 1605 | 1605 | 0 | 0 | 0 | 112 | 112 | 0 | 0 | 0
6 | BAY-7 | 4865096 | ELSTER | Kvarh(Lead/Lag) | 100 | 7481 | 7468 | 13 | 1300 | 0.0013 | 86788 | 86031 | 757 | 75700 | 0.0757
7 | BAY-37 | 4865097 | ELSTER | Kvarh(Lead/Lag) | 100 | 40708 | 40902 | -194 | -19400 | -0.0194 | 269301 | 269033 | 268 | 26800 | 0.0268
8 | BAY-9 | 4864789 | ELSTER | Kvarh(Lead/Lag) | 100 | 8384 | 8267 | 117 | 11700 | 0.0117 | 348116 | 345555 | 2561 | 256100 | 0.2561
9 | BAY-5 LAJPAT NAGAR | 4865181 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999973 | 999971 | 2 | 2000 | 0.002 | 999960 | 999710 | 250 | 250000 | 0.25
PAAPANKALAN
10 | Tx.1 | 4864973 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993088 | 993709 | -621 | 621000 | 0.621 | 961412 | 961547 | -135 | 135000 | 0.135
11 | Tx.2 | 4864974 | ELSTER | Kvarh(Lead/Lag) | -1000 | 991399 | 992116 | -717 | 717000 | 0.717 | 964186 | 964286 | -100 | 100000 | 0.1
12 | Tx.3 | 4864975 | ELSTER | Kvarh(Lead/Lag) | -1000 | 987851 | 988207 | -356 | 356000 | 0.356 | 948279 | 948420 | -141 | 141000 | 0.141
13 | Tx.4 | 4864976 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998437 | 999000 | -563 | 563000 | 0.563 | 964466 | 964577 | -111 | 111000 | 0.111
PAAPANKALAN-II
14 | Tx.1 | 5128437 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997063 | 998249 | -1186 | 1186000 | 1.186 | 993570 | 993618 | -48 | 48000 | 0.048
15 | Tx.2 | 5128439 | ELSTER | Kvarh(Lead/Lag) | -1000 | 5396 | 4513 | 883 | -883000 | -0.883 | 996777 | 996779 | -2 | 2000 | 0.002
NAJAFGARH
16 | Tx.1 | 4864969 | ELSTER | Kvarh(Lead/Lag) | -1000 | 41572 | 40617 | 955 | -955000 | -0.955 | 26191 | 26411 | -220 | 220000 | 0.22
17 | Tx.2 | 4864970 | ELSTER | Kvarh(Lead/Lag) | -1000 | 4386 | 4763 | -377 | 377000 | 0.377 | 10852 | 10990 | -138 | 138000 | 0.138
18 | Tx.3 | 4864971 | ELSTER | Kvarh(Lead/Lag) | -1000 | 25223 | 25128 | 95 | -95000 | -0.095 | 12240 | 12493 | -253 | 253000 | 0.253
19 | Tx.4 | 4864972 | ELSTER | Kvarh(Lead/Lag) | -1000 | 17433 | 16967 | 466 | -466000 | -0.466 | 42562 | 42611 | -49 | 49000 | 0.049
IMPORT
MANGOLPURI
21 | NANGLOI-2 (03) IMP. | 4864955 | ELSTER | Kvarh(Lead/Lag) | 1000 | 6003 | 5818 | 185 | 185000 | 0.185 | 4633 | 4522 | 111 | 111000 | 0.111
LODHI ROAD
22 | Tx.1 | 4864908 | ELSTER | Kvarh(Lead/Lag) | -1000 | 950149 | 953213 | -3064 | 3064000 | 3.064 | 906489 | 906489 | 0 | 0 | 0
23 | Tx.2 | 4864909 | ELSTER | Kvarh(Lead/Lag) | -1000 | 985583 | 985663 | -80 | 80000 | 0.08 | 870102 | 870102 | 0 | 0 | 0
OKHLA
24 | Tx.1 (66 KV) | 4864964 | ELSTER | Kvarh(Lead/Lag) | -1000 | 321 | 320 | 1 | -1000 | -0.001 | 992489 | 993551 | -1062 | 1062000 | 1.062
25 | Tx.2 (66 KV) | 4864965 | ELSTER | Kvarh(Lead/Lag) | -1000 | 445 | 445 | 0 | 0 | 0 | 976885 | 978660 | -1775 | 1775000 | 1.775
26 | Tx.1 (33 KV) | 4864890 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1053 | 368 | 685 | -685000 | -0.685 | 957901 | 957901 | 0 | 0 | 0
27 | Tx.2 (33 KV) | 4864891 | ELSTER | Kvarh(Lead/Lag) | -1000 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
28 | Tx.3 (33 KV) | 4864906 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999630 | 999630 | 0 | 0 | 0 | 911236 | 915557 | -4321 | 4321000 | 4.321
29 | Tx.4 (33 KV) | 4864907 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999027 | 999027 | 0 | 0 | 0 | 896885 | 901652 | -4767 | 4767000 | 4.767
BRPL(+) continue | [14 empty] | MARCH-2012
VASANT KUNJ
30 | Tx.1 | 4864988 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998857 | 998860 | -3 | 3000 | 0.003 | 975412 | 975970 | -558 | 558000 | 0.558
31 | Tx.2 | 4864989 | ELSTER | Kvarh(Lead/Lag) | -1000 | 53 | 55 | -2 | 2000 | 0.002 | 992658 | 993238 | -580 | 580000 | 0.58
32 | Tx.3 | 4864979 | ELSTER | Kvarh(Lead/Lag) | -2000 | 990611 | 990581 | 30 | -60000 | -0.06 | 972851 | 972722 | 129 | -258000 | -0.258
MEHRAULI
33 | Tx.1 | 4864966 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997761 | 997722 | 39 | -39000 | -0.039 | 932149 | 932216 | -67 | 67000 | 0.067
34 | Tx.2 | 4864967 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1529 | 1543 | -14 | 14000 | 0.014 | 945856 | 946658 | -802 | 802000 | 0.802
35 | Tx.3 | 4865048 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997696 | 997829 | -133 | 133000 | 0.133 | 938743 | 938801 | -58 | 58000 | 0.058
RIDGE VALLEY
36 | Tx-1 | 4864827 | ELSTER | Kvarh(Lead/Lag) | -666.666 | 999443 | 1000783 | -1340 | 893332.44 | 0.89333 | 597 | 597 | 0 | 0 | 0 | ROLL OVER
37 | Tx-2 | 4864828 | ELSTER | Kvarh(Lead/Lag) | -666.666 | 976937 | 980215 | -3278 | 2185331.148 | 2.1853 | 976467 | 976469 | -2 | 1333.332 | 0.0013333
DIAL
38 | Tx-1 | 4865024 | ELSTER | Kvarh(Lead/Lag) | -2000 | 521 | 432 | 89 | -178000 | -0.178 | 1157 | 1149 | 8 | -16000 | -0.016
39 | Tx-2 | 4864920 | ELSTER | Kvarh(Lead/Lag) | -2000 | 997294 | 997190 | 104 | -208000 | -0.208 | 412 | 405 | 7 | -14000 | -0.014
MASJID MOD
40 | Tx-1 | 5128414 | ELSTER | Kvarh(Lead/Lag) | -1000 | 983549 | 986910 | -3361 | 3361000 | 3.361 | 999915 | 999915 | 0 | 0 | 0
41 | Tx-2 | 5128416 | ELSTER | Kvarh(Lead/Lag) | -1000 | 983564 | 984559 | -995 | 995000 | 0.995 | 999997 | 999997 | 0 | 0 | 0
MUNDKA
42 | 66KV NANGLOI | 5100228 | ELSTER | Kvarh(Lead/Lag) | 800 | 999463 | 999263 | 200 | 160000 | 0.16 | 465 | 398 | 67 | 53600 | 0.0536
43 | 66KV NGL. WATER WORKS | 5128441 | ELSTER | Kvarh(Lead/Lag) | 800 | 3025 | 1697 | 1328 | 1062400 | 1.0624 | 224 | 184 | 40 | 32000 | 0.032
44 | 66KV DMRC | 5128443 | ELSTER | Kvarh(Lead/Lag) | 800 | 991057 | 992688 | -1631 | -1304800 | -1.3048 | 999903 | 999912 | -9 | -7200 | -0.0072
45 | 66KV NGL. T-OFF MGL P | 5128407 | ELSTER | Kvarh(Lead/Lag) | -2000 | 999898 | 999933 | -35 | 70000 | 0.07 | 0 | 0 | 0 | 0 | 0
PARK STREET
46 | 66KV R VALLEY-1 | 4864951 | ELSTER | Kvarh(Lead/Lag) | 1000 | 997432 | 998045 | -613 | -613000 | -0.613 | 38056 | 38077 | -21 | -21000 | -0.021
47 | 66KV R VALLEY-2 | 4902501 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 997353 | 997835 | -482 | -642665.06 | -0.64267 | 491 | 499 | -8 | -10666.64 | -0.010667
SARITA VIHAR
48 | TX-1 | 4864990 | ELSTER | Kvarh(Lead/Lag) | -1000 | 4578 | 3727 | 851 | -851000 | -0.851 | 981976 | 981988 | -12 | 12000 | 0.012
49 | Tx-2 | 4864991 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999374 | 999410 | -36 | 36000 | 0.036 | 989768 | 989773 | -5 | 5000 | 0.005
NARAINA
50 | GOPI NATH BAZAAR | 4865092 | ELSTER | Kvarh(Lead/Lag) | 100 | 6548 | 6347 | 201 | 20100 | 0.0201 | 9442 | 9245 | 197 | 19700 | 0.0197
SUDARSHAN PARK
51 | VISHAL | 4864792 | ELSTER | Kvarh(Lead/Lag) | 100 | 38246 | 38725 | -479 | -47900 | -0.0479 | 147056 | 147054 | 2 | 200 | 0.0002
REWARI LINE
52 | 33KV B/C | 4865170 | ELSTER | Kvarh(Lead/Lag) | 1000 | 0 | 0 | 0 | 0 | 0 | 999972 | 999972 | 0 | 0 | 0
KANJAWALA
53 | 66KV DMRC | 4864961 | ELSTER | Kvarh(Lead/Lag) | 1000 | 974433 | 975361 | -928 | -928000 | -0.928 | 992679 | 992681 | -2 | -2000 | -0.002
A.I.I.M.S.
54 | 11KV VIKAS SADAN | 4902586 | ELSTER | Kvarh(Lead/Lag) | 100 | 1449 | 1312 | 137 | 13700 | 0.0137 | 5351 | 5349 | 2 | 200 | 0.0002
55 | 11KV NDSE | 4902587 | ELSTER | Kvarh(Lead/Lag) | 100 | 8030 | 6740 | 1290 | 129000 | 0.129 | 12632 | 12620 | 12 | 1200 | 0.0012
SUM OF ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | 8.1638 |  |  |  |  | 16.528
BRPL (-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 % |  |  | MARCH-2012
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TILAK MARG
1 | EXHB-II | 4865143 | ELSTER | Kvarh(Lead/Lag) | -100 | 1001891 | 999619 | 2272 | -227200 | -0.2272 | 857955 | 857897 | 58 | -5800 | -0.0058 | ROLL OVER
EXPORT TO EAST & CENTRE
RIDGE VALLEY
2 | O/G SHANKAR RD.1 | 4865134 | ELSTER | Kvarh(Lead/Lag) | -100 | 91786 | 92317 | -531 | 53100 | 0.0531 | 1707 | 1707 | 0 | 0 | 0
3 | O/G SHANKAR RD.2 | 4865135 | ELSTER | Kvarh(Lead/Lag) | -100 | 59899 | 54266 | 5633 | -563300 | -0.5633 | 999577 | 999577 | 0 | 0 | 0
4 | KHYBER LANE-1 EXP. | 4864804 | ELSTER | Kvarh(Lead/Lag) | -100 | 999373 | 999645 | -272 | 27200 | 0.0272 | 999973 | 999973 | 0 | 0 | 0
5 | KHYBER LANE-2 EXP. | 4865163 | ELSTER | Kvarh(Lead/Lag) | -100 | 999264 | 999588 | -324 | 32400 | 0.0324 | 999997 | 999997 | 0 | 0 | 0
EXPORTS(*)
EXPORT TO NDMC
6 | SPM NO.1 | 4864845 | ELSTER | Kvarh(Lead/Lag) | -1000 | 632 | 668 | -36 | 36000 | 0.036 | 72621 | 72621 | 0 | 0 | 0
7 | SPM NO.2 | 4864852 | ELSTER | Kvarh(Lead/Lag) | -1000 | 6942 | 6009 | 933 | -933000 | -0.933 | 2117 | 2117 | 0 | 0 | 0
8 | NEHRU PARK | 4865142 | ELSTER | Kvarh(Lead/Lag) | -100 | 828626 | 818602 | 10024 | -1002400 | -1.0024 | 46063 | 46063 | 0 | 0 | 0
EXPORT TO NDMC
9 | SHAN NAGAR 1 | 4865093 | ELSTER | Kvarh(Lead/Lag) | -100 | 32250 | 29081 | 3169 | -316900 | -0.3169 | 51132 | 51155 | -23 | 2300 | 0.0023
10 | SHAN NAGAR 2 | 4865094 | ELSTER | Kvarh(Lead/Lag) | -100 | 27163 | 24419 | 2744 | -274400 | -0.2744 | 52655 | 52617 | 38 | -3800 | -0.0038
11 | VIDYUT BHAWAN | 4865144 | ELSTER | Kvarh(Lead/Lag) | -200 | 63422 | 64664 | -1242 | 248400 | 0.2484 | 103509 | 103509 | 0 | 0 | 0
EXPORTS(*)
A.I.I.M.S.
12 | TRANSFORMER-1 | 4865103 | ELSTER | Kvarh(Lead/Lag) | -100 | 42120 | 37947 | 4173 | -417300 | -0.4173 | 12543 | 12536 | 7 | -700 | -0.0007
13 | TRANSFORMER-2 | 4865132 | ELSTER | Kvarh(Lead/Lag) | -100 | 32690 | 32057 | 633 | -63300 | -0.0633 | 630921 | 629702 | 1219 | -121900 | -0.1219
14 | TRANSFORMER-3 | 4864803 | ELSTER | Kvarh(Lead/Lag) | -100 | 110198 | 102129 | 8069 | -806900 | -0.8069 | 231424 | 231401 | 23 | -2300 | -0.0023
KIDWAI NAGAR
15 | TR(10MVA)KILOKRI#2 | 4865133 | ELSTER | Kvarh(Lead/Lag) | -100 | 215395 | 205092 | 10303 | -1030300 | -1.0303 | 36220 | 36220 | 0 | 0 | 0
| Assessment on account of putting wrong M.F. (i.e.M.F.with + sign ) for mtr. No. 4865133 for period from 01/04/11 To 01/01/12 | [8 empty] | -2.082 |  |  |  |  | -0.7226
EXHIBITION I
16 | TILAK MARG | 4865076 | ELSTER | Kvarh(Lead/Lag) | -100 | 861 | 865 | -4 | 400 | 0.0004 | 12833 | 12707 | 126 | -12600 | -0.0126
17 | KRISHI BHAWAN | 4865077 | ELSTER | Kvarh(Lead/Lag) | -100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
REWARI LINE (ENERGY EXCHANGE WITH NDPL)
18 | 20 MVA TX.-2(Delv.) | 4864824 | ELSTER | Kvarh(Lead/Lag) | -100 | 14018 | 12630 | 1388 | -138800 | -0.1388 | 61784 | 61758 | 26 | -2600 | -0.0026
EXCHANGE OF ENERGY 11KV
EXPORTS
VISHAL
19 | RAMESH NAGAR-1 | 4865090 | ELSTER | Kvarh(Lead/Lag) | -100 | 8781 | 8429 | 352 | -35200 | -0.0352 | 13976 | 13734 | 242 | -24200 | -0.0242
20 | BALI NAGAR -1 | 4902519 | ELSTER | Kvarh(Lead/Lag) | -100 | 9668 | 9595 | 73 | -7300 | -0.0073 | 30964 | 30919 | 45 | -4500 | -0.0045
21 | ESI HOSPITAL | 4902520 | ELSTER | Kvarh(Lead/Lag) | -100 | 13752 | 13736 | 16 | -1600 | -0.0016 | 38042 | 37334 | 708 | -70800 | -0.0708
S.B.MILL
22 | MOTI NAGAR KIOSK | 4902521 | ELSTER | Kvarh(Lead/Lag) | -100 | 33100 | 32745 | 355 | -35500 | -0.0355 | 10957 | 10896 | 61 | -6100 | -0.0061
23 | 53 RAMA ROAD | 4902522 | ELSTER | Kvarh(Lead/Lag) | -100 | 840 | 840 | 0 | 0 | 0 | 185 | 185 | 0 | 0 | 0
24 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | -100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
25 | 70 RAMA ROAD | 4902524 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | MOTI NAGAR 2 | 4902525 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | NAJAFGARH ROAD | 4902526 | ELSTER | Kvarh(Lead/Lag) | -100 | 15843 | 15724 | 119 | -11900 | -0.0119 | 11244 | 11217 | 27 | -2700 | -0.0027
28 | PHILIPS | 4902527 | ELSTER | Kvarh(Lead/Lag) | -100 | 997311 | 997513 | -202 | 20200 | 0.0202 | 1324 | 1313 | 11 | -1100 | -0.0011
29 | ZAKHIRA | 4902528 | ELSTER | Kvarh(Lead/Lag) | -100 | 11525 | 11525 | 0 | 0 | 0 | 4086 | 4086 | 0 | 0 | 0
REWARI LINE (11KV TRANSFER OF ENERGY)
30 | BSES -NDPL(EX.) ON BUS-1&2 | 4865087 | ELSTER | Kvarh(Lead/Lag) | 400 | 4570 | 4570 | 0 | 0 | 0 | 12611 | 12610 | 1 | 400 | 0.0004
31 | BSES -NDPL(EX.) ON BUS-2&3 | 4902516 | ELSTER | Kvarh(Lead/Lag) | -100 | 999301 | 999305 | -4 | 400 | 0.0004 | 999393 | 999274 | 119 | -11900 | -0.0119
TOTAL OF ENERGY AT INTER COMPANY EXCHANGE POINTS | [9 empty] | -7.5292 |  |  |  |  | -0.9909
MARCH-2012
EXECUTIVE SUMMERY BSES R.P. LTD.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (REFER SHEET BRPL (+)) | [9 empty] | 8.1638 |  |  |  |  | 16.528
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet BRPL(-)) | [9 empty] | -7.5292 |  |  |  |  | -0.9909
3)ENERGY RECEIVED FROM ROHTAK ROAD (REFER ROHTAK ROAD SHEET ENC.) | [9 empty] | 1.5299 |  |  |  |  | 0.334
4) ENERGY RELEASED TO MES BY BRPL | [9 empty] | -0.2532 |  |  |  |  | -0.0964
NET ENERGY TO BSES RAJDHANI POWER LIMITED | [9 empty] | 1.9113 |  |  |  |  | 15.7747
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 1.9113 | (REACTIVE MUs) |  |  |  | 15.7747 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.1397 | (REACTIVE MUs) |  |  |  | 2.503 | (REACTIVE MUs)
[9 empty] | TOTAL | 1.7716 | (REACTIVE MUs) |  |  |  | 18.2777 | (REACTIVE MUs)

## NDMC
DELHI TRANSCO LIMITED | [15 empty] | MARCH-2012
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-NDMC
NDMC(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AT PARK STREET
EXPORT TO NDMC
1 | BAIRD RD.1 | 4865136 | ELSTER | Kvarh(Lead/Lag) | 200 | 24406 | 22606 | 1800 | 360000 | 0.36 | 62490 | 62452 | 38 | 7600 | 0.0076
2 | BAIRD RD.2 | 4865137 | ELSTER | Kvarh(Lead/Lag) | 100 | 38195 | 32631 | 5564 | 556400 | 0.5564 | 121505 | 121413 | 92 | 9200 | 0.0092
3 | NIRMAN BHAWAN | 4865138 | ELSTER | Kvarh(Lead/Lag) | 200 | 988843 | 989526 | -683 | -136600 | -0.1366 | 4293 | 4264 | 29 | 5800 | 0.0058
4 | H.LANE | 4865139 | ELSTER | Kvarh(Lead/Lag) | 200 | 44652 | 42190 | 2462 | 492400 | 0.4924 | 80321 | 80276 | 45 | 9000 | 0.009
5 | 66 KV BD MARG-I | 4864948 | ELSTER | Kvarh(Lead/Lag) | 1000 | 67410 | 67669 | -259 | -259000 | -0.259 | 232 | 232 | 0 | 0 | 0
6 | 66 KV BD MARG-II | 4864949 | ELSTER | Kvarh(Lead/Lag) | 1000 | 5877 | 3498 | 2379 | 2379000 | 2.379 | 54 | 54 | 0 | 0 | 0
7 | 66KV DMRC | 5128434 | ELSTER | Kvarh(Lead/Lag) | 800 | 994597 | 996079 | -1482 | -1185600 | -1.1856 | 998394 | 998437 | -43 | -34400 | -0.0344
8 | 66KV GUEST HOUSE | 5128445 | ELSTER | Kvarh(Lead/Lag) | 800 | 2398 | 1132 | 1266 | 1012800 | 1.0128 | 160 | 126 | 34 | 27200 | 0.0272
I.P.STATION EXPORT TO NDMC
9 | BAY-2 (N BWN) | 4865124 | ELSTER | Kvarh(Lead/Lag) | 100 | 998367 | 998349 | 18 | 1800 | 0.0018 | 287049 | 285439 | 1610 | 161000 | 0.161
10 | BAY-4 (E LANE) | 4865125 | ELSTER | Kvarh(Lead/Lag) | 100 | 6952 | 6862 | 90 | 9000 | 0.009 | 420168 | 418742 | 1426 | 142600 | 0.1426
11 | BAY-6 (T MARG) | 4865126 | ELSTER | Kvarh(Lead/Lag) | 100 | 11134 | 11127 | 7 | 700 | 0.0007 | 214859 | 209787 | 5072 | 507200 | 0.5072
12 | BAY-10 (E LANE) | 4865127 | ELSTER | Kvarh(Lead/Lag) | 100 | 5301 | 5369 | -68 | -6800 | -0.0068 | 301378 | 301840 | -462 | -46200 | -0.0462
13 | BAY-16 (N BWN) | 4865128 | ELSTER | Kvarh(Lead/Lag) | 100 | 998701 | 998703 | -2 | -200 | -0.0002 | 232057 | 231128 | 929 | 92900 | 0.0929
14 | BAY-28 (C PLACE) | 4865129 | ELSTER | Kvarh(Lead/Lag) | 100 | 93 | 103 | -10 | -1000 | -0.001 | 131089 | 130485 | 604 | 60400 | 0.0604
15 | BAY-38 (C PLACE) | 4865130 | ELSTER | Kvarh(Lead/Lag) | 100 | 12970 | 12683 | 287 | 28700 | 0.0287 | 193305 | 189784 | 3521 | 352100 | 0.3521
16 | BAY-42 (C PLACE) | 4865131 | ELSTER | Kvarh(Lead/Lag) | 100 | 13229 | 13085 | 144 | 14400 | 0.0144 | 230500 | 228182 | 2318 | 231800 | 0.2318
G.T.
17 | VIDYUT BHAWAN-1 | 4865037 | ELSTER | Kvarh(Lead/Lag) | 1100 | 0 | 0 | 0 | 0 | 0 | 56914 | 57387 | -473 | -520300 | -0.5203
18 | VIDYUT BHAWAN-2 | 4865038 | ELSTER | Kvarh(Lead/Lag) | 1000 | 4972 | 5064 | -92 | -92000 | -0.092 | 36470 | 36421 | 49 | 49000 | 0.049
19 | SCHOOL LANE-1 | 4865039 | ELSTER | Kvarh(Lead/Lag) | 1100 | 0 | 0 | 0 | 0 | 0 | 131186 | 131324 | -138 | -151800 | -0.1518
20 | SCHOOL LANE-2 | 4865040 | ELSTER | Kvarh(Lead/Lag) | 1000 | 8285 | 8040 | 245 | 245000 | 0.245 | 48402 | 48287 | 115 | 115000 | 0.115
[10 empty] | 0.153 |  |  |  |  | -0.5081
RIDGE VALLEY
21 | SPM NO.1 | 4864845 | ELSTER | Kvarh(Lead/Lag) | 1000 | 632 | 668 | -36 | -36000 | -0.036 | 72621 | 72621 | 0 | 0 | 0
22 | SPM NO.2 | 4864852 | ELSTER | Kvarh(Lead/Lag) | 1000 | 6942 | 6009 | 933 | 933000 | 0.933 | 2117 | 2117 | 0 | 0 | 0
23 | NEHRU PARK | 4865142 | ELSTER | Kvarh(Lead/Lag) | 100 | 828626 | 818602 | 10024 | 1002400 | 1.0024 | 46063 | 46063 | 0 | 0 | 0
24 | A.I.I.M.S.
25 | TX-I | 4865103 | ELSTER | Kvarh(Lag) | 100 | 42120 | 37947 | 4173 | 417300 | 0.4173 | 12543 | 12536 | 7 | 700 | 0.0007
26 | TX-2 | 4865132 | ELSTER | Kvarh(Lead/Lag) | 100 | 32690 | 32057 | 633 | 63300 | 0.0633 | 630921 | 629702 | 1219 | 121900 | 0.1219
27 | TX-3 | 4864803 | ELSTER | Kvarh(Lead/Lag) | 100 | 110198 | 102129 | 8069 | 806900 | 0.8069 | 231424 | 231401 | 23 | 2300 | 0.0023
MARCH-2012
NDMC(+) Continue…
KIDWAI NAGAR
28 | TR(10MVA) KILOKRI#2 | 4865133 | ELSTER | Kvarh(Lead/Lag) | 100 | 215395 | 205092 | 10303 | 1030300 | 1.0303 | 36220 | 36220 | 0 | 0 | 0
| Assessment on account of putting wrong M.F. (i.e.M.F.with - sign ) for mtr. No. 4865133 for period from 01/04/11 To 01/01/12 | [8 empty] | 2.082 |  |  |  |  | 0.7226
EXHIBITION I
29 | TILAK MARG | 4865076 | ELSTER | Kvarh(Lead/Lag) | 100 | 861 | 865 | -4 | -400 | -0.0004 | 12833 | 12707 | 126 | 12600 | 0.0126
30 | KRISHI BHAWAN | 4865077 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
LODHI ROAD
31 | SHAN NAGAR 1 | 4865093 | ELSTER | Kvarh(Lead/Lag) | 100 | 32250 | 29081 | 3169 | 316900 | 0.3169 | 51132 | 51155 | -23 | -2300 | -0.0023
32 | SHAN NAGAR 2 | 4865094 | ELSTER | Kvarh(Lead/Lag) | 100 | 27163 | 24419 | 2744 | 274400 | 0.2744 | 52655 | 52617 | 38 | 3800 | 0.0038
33 | VIDYUT BHAWAN (exp) | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 63422 | 64664 | -1242 | -248400 | -0.2484 | 103509 | 103509 | 0 | 0 | 0
TILAK MARG
34 | EXHB-II | 4865143 | ELSTER | Kvarh(Lag) | 100 | 1001891 | 999619 | 2272 | 227200 | 0.2272 | 857955 | 857897 | 58 | 5800 | 0.0058
NDMC(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AIIMS
1 | 11KV VIKAS SADAN | 4902586 | ELSTER | Kvarh(Lead/Lag) | -100 | 1449 | 1312 | 137 | -13700 | -0.0137 | 5351 | 5349 | 2 | -200 | -0.0002
2 | 11KV NDSE | 4902587 | ELSTER | Kvarh(Lead/Lag) | -100 | 8030 | 6740 | 1290 | -129000 | -0.129 | 12632 | 12620 | 12 | -1200 | -0.0012
TOTAL ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | 10.1452 |  |  |  |  | 1.8841
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
| ENERGY TO NDMC | [8 empty] | 10.1452 |  |  |  |  | 1.8841
| SHARED DISTRIBUTION GENERATED BY GENCO | [8 empty] | -0.017772 |  |  |  |  | 0.31843
| TOTAL ENERGY TO NDMC | [8 empty] | 10.1274 |  |  |  |  | 2.2025

## MES
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | MARCH-2012
CUSTOMER- MES
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
MES(+)
FED FROM DTL SYSTEM.
NARAINA ( ON 33KV)
1 | KHBR LANE-1-EXP. | 4864848 | ELSTER | Kvarh(Lead/Lag) | 1000 | 642 | 630 | 12 | 12000 | 0.012 | 14216 | 14174 | 42 | 42000 | 0.042
2 | KHBR LANE-2 -EXP. | 4864849 | ELSTER | Kvarh(Lead/Lag) | 1000 | 452 | 443 | 9 | 9000 | 0.009 | 18605 | 18560 | 45 | 45000 | 0.045
3 | KIRBY PLACE-1 | 4864846 | ELSTER | Kvarh(Lead/Lag) | 1000 | 822 | 803 | 19 | 19000 | 0.019 | 26496 | 26402 | 94 | 94000 | 0.094
4 | KIRBY PLACE-2 | 4864847 | ELSTER | Kvarh(Lead/Lag) | 1000 | 463 | 463 | 0 | 0 | 0 | 13601 | 13599 | 2 | 2000 | 0.002
5 | SHEKHAWATI | 4864850 | ELSTER | Kvarh(Lead/Lag) | 1000 | 2121 | 1939 | 182 | 182000 | 0.182 | 6760 | 6756 | 4 | 4000 | 0.004
RIDGE VALLEY ON 33KV
6 | KHBR LANE-1 -EXP | 4864804 | ELSTER | Kvarh(Lead/Lag) | 100 | 999373 | 999645 | -272 | -27200 | -0.0272 | 999973 | 999973 | 0 | 0 | 0
7 | KHBR LANE-2 -EXP. | 4865163 | ELSTER | Kvarh(Lead/Lag) | 100 | 999264 | 999588 | -324 | -32400 | -0.0324 | 999997 | 999997 | 0 | 0 | 0
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.1624 |  |  |  |  | 0.187
FED FROM BSES RAJDHANI POWER LIMITED (11KV)
8 | SIGNAL ENCLAVE | 4865065 | ELSTER | Kvarh(Lead/Lag) | 100 | 3287 | 3287 | 0 | 0 | 0 | 32963 | 32963 | 0 | 0 | 0
9 | R.R. HOSPITAL | 4865066 | ELSTER | Kvarh(Lead/Lag) | 100 | 28798 | 27780 | 1018 | 101800 | 0.1018 | 59487 | 59395 | 92 | 9200 | 0.0092
10 | DEFENCE CLUB | 4865067 | ELSTER | Kvarh(Lead/Lag) | 100 | 66686 | 66427 | 259 | 25900 | 0.0259 | 7181 | 7140 | 41 | 4100 | 0.0041
11 | SUBROTO PARK | 4865078 | ELSTER | Kvarh(Lead/Lag) | 100 | 20361 | 19647 | 714 | 71400 | 0.0714 | 46440 | 46245 | 195 | 19500 | 0.0195
12 | SUBROTO PARK | 4865079 | ELSTER | Kvarh(Lead/Lag) | 100 | 999972 | 999895 | 77 | 7700 | 0.0077 | 17869 | 17623 | 246 | 24600 | 0.0246
13 | BI LINES | 4865080 | ELSTER | Kvarh(Lead/Lag) | 100 | 76815 | 76550 | 265 | 26500 | 0.0265 | 40234 | 39980 | 254 | 25400 | 0.0254
14 | BI LINES | 4865081 | ELSTER | Kvarh(Lead/Lag) | 100 | 2796 | 2597 | 199 | 19900 | 0.0199 | 3904 | 3768 | 136 | 13600 | 0.0136
TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [9 empty] | 0.2532 |  |  |  |  | 0.0964
MES(-)
FED TO BSES RAJDHANI POWER LIMITED (11KV)
15 | BOOSTER PUMP | 4902545 | ELSTER | Kvarh(Lead/Lag) | 50 | 7848 | 7848 | 0 | 0 | 0 | 18966 | 18966 | 0 | 0 | 0
TOTAL FED TO BSES RAJDHANI POWER LIMITED (11KV) | [9 empty] | 0 |  |  |  |  | 0
| TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [8 empty] | 0.2532 |  |  |  |  | 0.0964
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.1624 |  |  |  |  | 0.187
| GRAND TOTAL (BSES RPL+NDPL+DTL) | [8 empty] | 0.4156 |  |  |  |  | 0.2834
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 0.4156 | (REACTIVE MUs) |  |  |  | 0.2834 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | -0.0030471 | (REACTIVE MUs) |  |  |  | 0.054596 | (REACTIVE MUs)
[9 empty] | TOTAL | 0.41255 | (REACTIVE MUs) |  |  |  | 0.338 | (REACTIVE MUs)

## ROHTAK ROAD
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | MARCH-2012
ROHTAK ROAD
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TO BSES RAJDHANI
AT 33 KV LEVEL
1 | O/G SBMILL-1 | 4864796 | ELSTER | Kvarh(Lead/Lag) | 100 | 58294 | 58210 | 84 | 8400 | 0.0084 | 77749 | 77742 | 7 | 700 | 0.0007
2 | O/G SBMILL-2 | 4864797 | ELSTER | Kvarh(Lead/Lag) | 100 | 8716 | 7464 | 1252 | 125200 | 0.1252 | 999467 | 999463 | 4 | 400 | 0.0004
3 | O/G VISHAL-1 | 4864818 | ELSTER | Kvarh(Lead/Lag) | 100 | 173471 | 171028 | 2443 | 244300 | 0.2443 | 91994 | 91972 | 22 | 2200 | 0.0022
4 | O/G MADI PUR | 4864842 | ELSTER | Kvarh(Lead/Lag) | 1000 | 16753 | 15812 | 941 | 941000 | 0.941 | 17797 | 17795 | 2 | 2000 | 0.002 | YCT Changes from 800/1 to 750/1 on dated 28/03/12
4 | O/G MADI PUR | 4864842 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 16777 | 16753 | 24 | 22500 | 0.0225 | 17797 | 17797 | 0 | 0 | 0
AT 33/11 KV LEVEL
5 | TX.-I | 4864880 | ELSTER | Kvarh(Lead/Lag) | -500 | 993256 | 993554 | -298 | 149000 | 0.149 | 943863 | 944146 | -283 | 141500 | 0.1415
6 | TX-II | 4864881 | ELSTER | Kvarh(Lead/Lag) | -500 | 994098 | 994177 | -79 | 39500 | 0.0395 | 986629 | 987004 | -375 | 187500 | 0.1875
7 | B/C (IMP.TO BRPL) | 4902572 | ELSTER | Kvarh(Lead/Lag) | 300 | 999987 | 999987 | 0 | 0 | 0 | 999883 | 999884 | -1 | -300 | -0.0003
| TOTAL BSES RAJDHANI PO.LTD. | [8 empty] | 1.5299 |  |  |  |  | 0.334
TO BSES YAMUNA PO. LTD.
AT 33 KV LEVEL
8 | O/G FAIZ ROAD | 4864794 | ELSTER | Kvarh(Lead/Lag) | 200 | 952502 | 954014 | -1512 | -302400 | -0.3024 | 991980 | 991982 | -2 | -400 | -0.0004
9 | O/G DMS | 4864795 | ELSTER | Kvarh(Lead/Lag) | 100 | 871326 | 881275 | -9949 | -994900 | -0.9949 | 928495 | 928504 | -9 | -900 | -0.0009
| TOTAL (BSES Y.P.L.) | [8 empty] | -1.2973 |  |  |  |  | -0.0013
TO NORTH DELHI POWER LIMITED
AT 33 KV LEVEL
10 | O/G VISHAL-2 | 4864819 | ELSTER | Kvarh(Lead/Lag) | 200 | 170331 | 167339 | 2992 | 598400 | 0.5984 | 258656 | 258649 | 7 | 1400 | 0.0014
11 | O/G 33KV RAMPURA-1 | 4864801 | ELSTER | Kvarh(Lead/Lag) | 200 | 61528 | 57645 | 3883 | 776600 | 0.7766 | 40209 | 40209 | 0 | 0 | 0
12 | O/G 33KV RAMPURA-2 | 4864820 | ELSTER | Kvarh(Lead/Lag) | 100 | 87301 | 79666 | 7635 | 763500 | 0.7635 | 69975 | 69980 | -5 | -500 | -0.0005
13 | O/G 33KV SH.W.BAGH-I | 4865168 | ELSTER | Kvarh(Lead/Lag) | 1000 | 987316 | 987310 | 6 | 6000 | 0.006 | 997819 | 997816 | 3 | 3000 | 0.003
14 | O/G 33KV SH.W.BAGH-2 | 4864802 | ELSTER | Kvarh(Lead/Lag) | 100 | 982411 | 983463 | -1052 | -105200 | -0.1052 | 7390 | 7391 | -1 | -100 | -0.0001
15 | O/G 33KV KIRTI NAGAR | 5128400 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 999993 | 1000040 | -47 | -44062.5 | -0.044062 | 2834 | 2773 | 61 | 57187.5 | 0.057188 | ROLL OVER
AT 33/11 KV LEVEL
16 | TX-III | 4864882 | ELSTER | Kvarh(Lead/Lag) | -500 | 992142 | 992222 | -80 | 40000 | 0.04 | 995715 | 995715 | 0 | 0 | 0 | YCT Changes from 400/1 to 500/1 on dated 21/03/12
16 | TX-III | 4864882 | ELSTER | Kvarh(Lead/Lag) | -625 | 992083 | 992142 | -59 | 36875 | 0.036875 | 995715 | 995715 | 0 | 0 | 0
17 | B/C (IMP.TO NDPL) | 4902572 | ELSTER | Kvarh(Lead/Lag) | -300 | 999987 | 999987 | 0 | 0 | 0 | 999883 | 999884 | -1 | 300 | 0.0003
| TOTAL NDPL | [8 empty] | 2.0721 |  |  |  |  | 0.061288
| E) NET EXPORT TO BSES RPL | [8 empty] | 1.5299 |  |  |  |  | 0.334
| F) NET EXPORT TO BSES YPL | [8 empty] | -1.2973 |  |  |  |  | -0.0013
| G) NET EXPORT TO N.D.P.L. | [8 empty] | 2.0721 |  |  |  |  | 0.061288

## STEPPED UP GENCO
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | MARCH-2012
A.) EXPORT/IMPORT OF REACTIVE ENERGY IN LEAD/LAG MODE ON IBT's AT GENCO
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | REMARK
G.T.
| (66KV ) | (EXPORT)
1 | IBT-I | 4902497 | ELSTER | kvarh (Lead/lag) | 2000 | 6102 | 6539 | -437 | -874000 | -0.874 | 999985 | 1000013 | -28 | -56000 | -0.056
2 | IBT-2 | 4902498 | ELSTER | kvarh (Lead/lag) | 2000 | 8704 | 8052 | 652 | 1304000 | 1.304 | 137 | 55 | 82 | 164000 | 0.164
[7 empty] | NET REACTIVE ENERGY |  |  | 0.43 |  | NET REACTIVE ENERGY |  |  | 0.108
RPH
| (33KV ) | (EXPORT)
3 | IBT-I | 4902505 | ELSTER | kvarh (Lead/lag) | 1000 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 | IBT-2 | 4902506 | ELSTER | kvarh (Lead/lag) | 1000 | 985515 | 985552 | -37 | -37000 | -0.037 | 986183 | 988909 | -2726 | -2726000 | -2.726
[7 empty] | NET REACTIVE ENERGY |  |  | -0.037 |  | NET REACTIVE ENERGY |  |  | -2.726
1)TOTAL NET REACTIVE ENERGY FROM GENCO AT 66/33KV LEVEL | [9 empty] | 0.393 |  |  |  |  | -2.618
B) | REACTIVE ENERGY DRAWL ON FEEDERS FROM GENCO BY
[7 empty] | NDPL = |  |  | 0 |  |  |  |  | 0
[7 empty] | BRPL = |  |  | 0 |  |  |  |  | 0
[7 empty] | BYPL = |  |  | -0.2136 |  |  |  |  | -2.8296
[7 empty] | NDMC = |  |  | 0.153 |  |  |  |  | -0.5081
MES =
[7 empty] | 2)TOTAL |  |  | -0.0606 |  |  |  |  | -3.3377
C) TOTAL REACTIVE ENERGY TO BE DISTRIBUTED AMONGS DISCOMs [1+2]= | [9 empty] | 0.3324 |  |  |  |  | -5.9557
D). | SHARE OF EACH DISCOM TO BE DISTRIBUTED ON PROPORTION TO THEIR ACTIVE ENERGY DRAWAL OF C
1) | NDPL | (ACTIVE ENERGY DRAWL= |  |  |  | 28.3068 | % |  |  | 0.094092 |  |  |  |  | -1.6859
2) | BRPL | (ACTIVE ENERGY DRAWL= |  |  |  | 42.0274 | % |  |  | 0.1397 |  |  |  |  | -2.503
3) | BYPL | (ACTIVE ENERGY DRAWL= |  |  |  | 23.4025 | % |  |  | 0.07779 |  |  |  |  | -1.3938
4) | NDMC | (ACTIVE ENERGY DRAWL= |  |  |  | 5.3466 | % |  |  | 0.017772 |  |  |  |  | -0.31843
5) | MES | (ACTIVE ENERGY DRAWL= |  |  |  | 0.9167 | % |  |  | 0.0030471 |  |  |  |  | -0.054596
Note :Sharing taken from wk-50 abt bill 2011-12

## FINAL EX. SUMMARY
DELHI TRANSCO LIMITED
REACTIVE ENERGY RELEASE STATEMENT TO LICENSEES.
PERIOD 1st MARCH-2012 TO 31st MARCH-2012
FINAL EXECUTIVE SUMMERY
[6 empty] | Energy for above 103% |  | Energy for below 97%
1 | NET REACTIVE ENERGY TO N.D.P.L. |  |  |  | + | 2.7116 | + | 3.0602
2 | NET REACTIVE ENERGY TO BSES RAJDHANI PO.LTD. |  |  |  | + | 1.7716 | + | 18.2777
3 | NET REACTIVE ENERGY TO BSES YAMUNA PO.LTD. |  |  |  | + | 3.7748 | + | 3.8248
4 | NET REACTIVE ENERGY TO NDMC |  |  |  | + | 10.1274 | + | 2.2025
5 | NET REACTIVE ENERGY TO MES |  |  |  | + | 0.41255 | + | 0.338
ALL FIGURES IN Mus.
Note:-
+ve sign indicates reactive energy drawl from the grid/system
-ve sign indicates reactive energy injected to the grid/system
Assessment of 20MVA Tx. AT KIDWAI NAGAR (Meter No. 4865133) for the period April 2011 to December 2011 due to wrong M.F.. The total assessment is (-)6.246Mus on above 103%
and (-)2.1678Mus on below 97%. The assessment to be distributed equally in the month of Jan., Feb, March 2012

## PRAGATI
[8 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIEVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/04/12 | INTIAL READING 01/03/12 | DIFF. | CONSP. | REACTIVE MUs
PRAGATI
| (220 KV) | (EXPORT)
1 | GT-I | 4902492 | ELSTER | kvarh (lag) | 1500 | 977434 | 979680 | -2246 | -3369000 | -3.369 | 981175 | 981175 | 0 | 0 | 0
2 | GT-II | 4902493 | ELSTER | kvarh (lag) | 1500 | 975571 | 975553 | 18 | 27000 | 0.027 | 986801 | 986820 | -19 | -28500 | -0.0285
3 | STG-III | 4902494 | ELSTER | kvarh (lag) | 1500 | 930170 | 930877 | -707 | -1060500 | -1.0605 | 970178 | 970187 | -9 | -13500 | -0.0135
[8 empty] | NET REACTIVE ENERGY |  | -4.4025 |  |  | NET REACTIVE ENERGY |  | -0.042
I.P.STATION
| (33KV) | (EXPORT)
1 | IBT-I | 4902509 | ELSTER | kvarh (lag) | 5000 | 997226 | 997179 | 47 | 235000 | 0.235 | 36729 | 36920 | -191 | -955000 | -0.955
2 | IBT-2 | 4902510 | ELSTER | kvarh (lag) | 1000 | 999433 | 999433 | 0 | 0 | 0 | 8097 | 8123 | -26 | -26000 | -0.026
3 | IBT-3 | 4864947 | ELSTER | kvarh (lag) | 1000 | 970216 | 970556 | -340 | -340000 | -0.34 | 990594 | 990881 | -287 | -287000 | -0.287
[8 empty] | NET REACTIVE ENERGY |  | -0.105 |  |  | NET REACTIVE ENERGY |  | -1.268