DELHI TRANSCO LTD.

STATE LOAD DISPATCH CENTER

PROGRESS REPORT

*****************

FEBRUARY - 2010

| S. No. | CONTENTS | Page No. |
| --- | --- | --- |
| 1. | Salient Features of Delhi Power System | 3 |
| 2. | Performance of Generating Stations within Delhi | 4 |
| 3. | Details of Outage of Generating Stations within Delhi | 5-23 |
| 4. | Allocation of Power to Delhi from unallocated quota of central sector | 24-26 |
| 5. | Allocation of Power to Discoms | 27 |
| 6. | Power Availability Demand Position of Delhi at the time of occurrence of Peak Demand | 28 |
| 7. | Power Availability Demand Position of Delhi at the time of occurrence of Maximum Un-Restricted Demand | 29 |
| 8. | Source wise scheduled drawl from grid and Availability within Delhi | 30-32 |
| 9. | Shedding Details | 33-36 |
| 10. | Load Curve for the Day of Peak Demand | 37 |
| 11. | Load Curve for the day of occurrence of Maximum Un-Restricted Demand | 38 |
| 12. | Load Curve for the day of Maximum Energy Consumed | 39 |
| 13. | Load Curve for the day of Maximum Un-Restricted Energy Demand | 40 |
| 14. | Load Duration Curve | 41 |
| 15. | Frequency Analysis | 42 |
| 16. | Voltage Profile for significant 220kV Sub-Stations | 43 |
| 17. | Voltage Profile for significant 400kV Sub-Stations | 44-45 |
| 18. | Details of Capacitors Installations in Delhi | 46-53 |
| 19. | Tripping Details of 400/220 KV System in Delhi Power System | 54-55 |
| 20. | Details of Under frequency Relay operations in Delhi Power System | 56 |

1	Salient Features of Delhi Power System

| Sr. No. | Features | FEB 2010 | FEB 2009 |
| --- | --- | --- | --- |
| 1 | Effective Generation Capacity within Delhi in MW |  |  |
|  | Indraprastha Power Station | 247.5 | 247.5 |
|  | Rajghat Power House | 135 | 135 |
|  | Gas Turbine | 270 | 282 |
|  | Pragati Power Corporation Ltd. | 330 | 330 |
|  | Badapur Thermal Power Station | 705 | 705 |
|  | Total | 1687.5 | 1699.5 |
| 2 | Maximum Unrestricted Demand (MW) | 3196 | 3105 |
|  | Date | 12.02.2010 | 13.02.2009 |
|  | Time | 10:04:55 | 07.47.48 |
| 3 | Peak Demand met (MW) | 3196 | 3105 |
|  | Date | 12.02.2010 | 13.02.2009 |
|  | Time | 10:04:55 | 07.47.48 |
| 4 | Peak Availability (MW) | 3382 | 2857 |
| 5 | Shortage (-) / Surplus (+) in MW | 186 | (-)248 |
| 6 | Percentage Shortage (-) / Surplus (+) | 5.82 | -7.99 |
| 7 | Maximum Energy Consume in a day (Mus) | 53.344 | 52.692 |
| 8 | Energy Consumed during the month | 1411.817 | 1388.129 |
| 9 | Load Shedding in Mus |  |  |
| A) | Due to Grid Restrictions |  |  |
| i) | Under Frequency Relay Operations | 0.000 | 0.430 |
| ii) | Manual Load shedding from DTL S/Stns. | 0.000 | 0.000 |
| iii) | Load Shedding due to low frequency / Low Voltage / TTC/ATC Violation |  |  |
|  | NDPL | 0.000 | 0.400 |
|  | BRPL | 0.000 | 1.779 |
|  | BYPL | 0.000 | 0.553 |
|  | NDMC | 0.000 | 0.000 |
|  | MES | 0.000 | 0.000 |
| iv) | Due to transmission Constraints in Central Sector | 0.000 | 0.000 |
|  | Total due to Grid Restriction | 0.000 | 3.162 |
| B) | Due to Constraints in System in Mus |  |  |
|  | DTL | 0.614 | 0.122 |
|  | NDPL | 4.031 | 3.317 |
|  | BRPL | 0.401 | 1.970 |
|  | BYPL | 0.156 | 0.265 |
|  | NDMC | 0.000 | 0.000 |
|  | MES | 0.000 | 0.000 |
|  | Other Agencies | 0.021 | 0.022 |
|  | Total | 5.223 | 5.696 |
| 11 | Grand Total in Mus | 5.223 | 8.858 |

2.	PERFORMANCE OF GENERATING STATIONS WITHIN DELHI DURING FEB. 2010

A)  For the month of February 2010

All Figures in MUs

| S. No | Stations | Gross Generation | Aux. Consumption | Net Generation | Availability (%) | Backing Down |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | IP | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 2. | RPH | 30.39500 | 4.67100 | 25.724 | 32.61 | 0.00000 |
| 3. | GT | 111.51900 | 4.18700 | 107.332 | 68.90 | 8.29850 |
| 4. | PPCL | 188.78600 | 4.77400 | 184.012 | 89.39 | 11.21700 |
| 5. | BTPS | 316.04965 | 34.76546 | 281.28419 | 68.69 | 16.13463 |
|  | TOTAL | 646.74965 | 48.39746 | 598.35219 |  | 35.65013 |

B) For the Year 2009-10 (Upto February 2010)

| Power Station | Effective Capacity (MW) | Net Gene- ration in MUs For Feb 10 | Avail -ability (%) For Feb.’10 | PLF (%) For Feb. 10 | Cumulative Generation in MUs upto Feb 10 for the year 2009-10 | Cumulative Availability in % upto Feb. 10 for the year 2009-10 | Cumulative PLF in % upto Feb 10 for the year 2009-10 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| IP | 247.5 | 0.000 | 0.000 | -- | 386.16600 | -- | -- |
| RPH | 135 | 25.724 | 32.61 | 32.61 | 478.71200 | 51.84 | 51.84 |
| GT | 282 | 107.332 | 68.90 | 64.19 | 1333.08000 | 74.16 | 63.51 |
| PPCL | 330 | 184.012 | 89.39 | 84.17 | 2161.67100 | 84.72 | 83.41 |
| BTPS | 705 | 281.28419 | 68.69 | 64.86 | 4374.97465 | 87.96 | 85.63 |
| TOTAL | 1699.5 | 598.35219 |  |  | 8734.60365 |  |  |

3	DETAILS OF OUTAGES OF GENERATING STNS. WITHIN DELHI W.E.F. APRIL 2009

(A)  IP STATION

| Unit no. | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 62.5 | 03.04.09 | 07.02 | 03.04.09 | 08.58 | D- Rediator Level not maintained. |
|  |  | 03.04.09 | 09.35 | 05.04.09 | 07.25 | Loss of excitation |
|  |  | 21.04.09 | 05.22 | 27.04.09 | 23.05 | Boiler Tube Leakage |
|  |  | 17.05.09 | 00.07 | 19.05.09 | 12.03 | Problem in Bottom System |
|  |  | 19.05.09 | 21.20 | 20.05.09 | 02.15 | Low vacuum |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 16.15 | Due to tripping of associated transmission lines. |
|  |  | 01.06.09 | 09.25 | 01.06.09 | 11.08 |  |
|  |  | 05.06.09 | 15.08 | 05.06.09 | 16.40 |  |
|  |  | 15.06.09 | 13.32 | 15.06.9 | 14.30 |  |
|  |  | 29.06.09 | 22.50 | 01.07.09 | 15.45 | Boiler Tube Leakage |
|  |  | 06.07.09 | 12.40 | 06.07.09 | 13.53 | Fire out. |
|  |  | 14.07.09 | 09.40 | 14.07.09 | 11.35 | Due to tripping of associated transmission lines. |
|  |  | 28.07.09 | 10.53 | 28.07.09 | 20.15 | Steam line burnt |
|  |  | 03.08.09 | 05.05 | 03.08.09 | 17.52 | Problem in Boiler Feed Pump |
|  |  | 11.08.09 | 17.50 | 13.08.09 | 07.40 | Boiler Tube Leakage |
|  |  | 27.08.09 | 17.30 | 08.09.09 | 20.28 | Due to tripping of associated transmission lines. Could not synchronized due to Durator Valve Knob |
|  |  | 11.09.09 | 07.55 | 11.09.09 | 14.42 | CHP Problem |
|  |  | 12.09.09 | 11.25 | 15.09.09 | 07.58 | Boiler Tube Leakage |
|  |  | 26.09.09 | 21.45 | 29.09.09 | 17.52 | Steam Leakage in Turbine |
|  |  | 29.09.09 | 20.15 | 30.09.09 | 08.18 | Generator Stator Temp High |
|  |  | 08.10.09 | 18.18 | 11.10.09 | 13.42 | Boiler Tube Leakage |
|  |  | 26.10.09 | 09.25 | 26.10.09 | 21.40 | No Coal flow |
|  |  | 27.10.09 | 05.58 | 27.10.09 | 09.10 | No Coal flow |
|  |  | 31.10.09 | 21.40 |  |  | Unit stopped |
| 3 | 62.5 | 06.04.09 | 13.38 | 09.04.09 | 07.07 | Boiler Tube Leakage |
|  |  | 06.05.09 | 06.30 | 08.05.09 | 21.55 | Boiler Tube Leakage |
|  |  | 19.05.09 | 21.11 | 20.05.09 | 04.58 | Low vacuum |
|  |  | 28.05.09 | 09.22 | 28.05.09 | 11.35 | Bus differential operation. |
|  |  | 01.06.09 | 09.29 | 01.06.09 | 11.52 | Due to tripping of associated transmission lines. |
|  |  | 10.06.09 | 09.52 | 10.06.09 | 12.10 | Vacuum Problem |
|  |  | 14.06.09 | 00.01 | 28.06.09 | 08.35 | Boiler Tube Leakage |
|  |  | 12.07.09 | 10.50 | 15.07.09 | 00.12 | Boiler Tube Leakage |
|  |  | 31.07.09 | 20.30 | 01.08.09 | 04.44 | Due to jerk |
|  |  | 02.08.09 | 22.58 | 03.08.09 | 10.30 | Low coal flow |
|  |  | 05.08.09 | 00.10 | 08.08.09 | 01.50 | Condenser Tube Leakage |
|  |  | 11.08.09 | 09.30 | 11.08.09 | 15.43 | No Coal Flow |
|  |  | 17.08.09 | 08.55 | 17.08.09 | 11.43 | Due to tripping of associated transmission lines. |
|  |  | 17.08.09 | 14.01 | 18.08.09 | 23.55 | Problem in Coal Bunker |
|  |  | 24.08.09 | 21.10 | 25.08.09 | 20.25 | Shortage of DM Water. |
|  |  | 27.08.09 | 17.50 | 28.08.09 | 00.50 | Due to tripping of associated transmission lines. |
|  |  | 28.08.09 | 22.50 | 06.09.09 | 14.02 | Boiler Tube Leakage |
|  |  | 08.09.09 | 23.40 | 09.09.09 | 20.20 | Condenser Tube Leakage |
|  |  | 24.09.09 | 12.15 | 27.09.09 | 07.30 | ID Fan problem |
|  |  | 04.10.09 | 09.35 | 05.10.09 | 09.50 | Leakage in Control Valve Pipe |
|  |  | 20.10.09 | 23.55 | 23.10.09 | 07.20 | Coal Mill Problem |
|  |  | 28.10.09 | 21.30 |  |  | Unit stopped |

| Unit no. | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 4 | 62.5 | 04.04.09 | 10.30 | 04.04.09 | 12.32 | Electrocution Trip Device Alarm |
|  |  | 29.04.09 | 05.10 | 29.04.09 | 09.35 | Coal mill problem |
|  |  | 29.04.09 | 12.43 | 13.05.09 | 16.43 | Main Buchloz Relay Operated(Tx-4) |
|  |  | 19.05.09 | 21.11 | 24.05.09 | 15.05 | Low vacuum |
|  |  | 25.05.09 | 19.42 | 27.05.09 | 23.15 | Boiler Tube Leakage |
|  |  | 28.05.09 | 09.25 | 28.05.09 | 10.34 | Bus differential operation. |
|  |  | 01.06.09 | 09.25 | 12.06 | 18.45 | Reduction Gear Problem |
|  |  | 15.06.09 | 13.32 | 15.06.09 | 15.10 | Due to tripping of associated transmission lines. |
|  |  | 22.06.09 | 20.57 | 24.06.09 | 04.40 | Boiler Tube Leakage |
|  |  | 29.06.09 | 22.50 | 30.06.09 | 01.40 | Due to tripping of associated transmission lines. |
|  |  | 04.07.09 | 06.00 | 15.07.09 | 16.25 | Shortage of DM water |
|  |  | 26.07.09 | 15.55 | 27.07.09 | 07.12 | Due to fire in boiler |
|  |  | 28.07.09 | 05.30 | 30.07.09 | 01.10 | Shortage of coal |
|  |  | 03.08.09 | 07.30 | 03.08.09 | 08.58 | Low Vacuum |
|  |  | 10.08.09 | 04.25 | 10.08.09 | 22.55 | Coal Bunker Empty |
|  |  | 17.08.09 | 08.55 | 17.08.09 | 10.05 | Coal Bunker Empty |
|  |  | 18.08.09 | 05.40 | 18.05.09 | 06.58 | Low Coal Flow |
|  |  | 18.08.09 | 07.10 | 28.08.09 | 11.55 | Condenser Tube Leakage |
|  |  | 28.08.09 | 14.45 | 29.08.09 | 13.12 | Heavy Steam Leakage in Boiler |
|  |  | 04.09.09 | 01.55 | 04.09.09 | 11.32 | Tripped on ETD |
|  |  | 04.09.09 | 14.40 | 06.09.09 | 04.45 | Boiler Tube Leakage |
|  |  | 12.09.09 | 16.37 | 12.09.09 | 20.55 | Fire out |
|  |  | 17.09.09 | 19.45 | 19.09.09 | 23.55 | Boiler Tube Leakage |
|  |  | 03.10.09 | 18.27 | 17.10.09 | 05.30 | Boiler Tube Leakage |
|  |  | 20.10.09 | 07.25 | 20.10.09 | 07.20 | Coal mill problem |
|  |  | 20.10.09 | 23.55 | 23.10.09 | 15.16 | Coal mill problem |
|  |  | 26.10.09 | 15.35 | 28.10.09 | 21.40 | No coal availability |
|  |  | 29.10.09 | 18.22 | 29.10.09 | 22.50 | No coal availability |
|  |  | 29.10.09 | 23.07 | 30.10.09 | 00.10 | Heat Control valve leakage |
|  |  | 01.11.09 | 00.10 | 01.11.09 | 10.35 | No coal availability |
|  |  | 02.11.09 | 13.47 | 02.11.09 | 17.18 | Water level low |
|  |  | 03.11.09 | 10.15 | 04.11.09 | 17.34 | No coal availability |
|  |  | 05.11.09 | 03.58 | 05.11.09 | 05.00 | No coal availability |
|  |  | 05.11.09 | 09.12 | 05.11.09 | 18.18 | No coal availability |
|  |  | 05.11.09 | 16.28 | 09.11.09 | 15.20 | No coal availability |
|  |  | 10.11.09 | 21.40 | 24.11.09 | 13.40 | Boiler Tube Leakage |
|  |  | 24.11.09 | 13.50 | 26.11.09 | 14.00 | Boiler Tube Leakage |
|  |  | 27.11.09 | 18.10 | 27.11.09 | 20.45 | No coal availability |
|  |  | 28.11.09 | 13.55 | 28.11.09 | 16.55 | No coal availability |
| 5 | 60 | 31.03.09 | 04.03 | 04.04.09 | 05.58 | Electrocution Trip Device Alarm |
|  |  | 09.04.09 | 02.40 | 12.04.09 | 00.35 | Boiler Tube Leakage |
|  |  | 12.04.09 | 17.40 | 15.04.09 | 16.45 | Electrocution Trip Device Alarm |
|  |  | 15.04.09 | 19.43 | 18.04.09 | 23.17 | Electrocution Trip Device Alarm |
|  |  | 22.04.09 | 19.02 | 24.04.09 | 16.00 | Condenser Tube Leakage |
|  |  | 04.05.09 | 09.45 | 04.05.09 | 10.26 | Tripped due to jerk due to tripping of 33kV Bay-29 |
|  |  | 04.05.09 | 20.56 | 11.05.09 | 05.15 | Fire in PA Fan |
|  |  | 15.05.09 | 23.18 | 16.05.09 | 07.40 | Problem in RC Feeder |

| Unit no. | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 5 | 60 | 18.05.09 | 13.10 | 05.07.09 | 03.45 | ID Fan Problem |
|  |  | 05.07.09 | 07.00 | 08.07.09 | 02.35 | Boiler Tube Leakage |
|  |  | 08.07.09 | 10.30 | 12.07.09 | 03.24 | Condenser Tube Leakage |
|  |  | 13.07.09 | 06.50 | 13.07.09 | 07.05 | Drum level high |
|  |  | 13.07.09 | 07.50 | 13.07.09 | 23.25 | Shortage of DM water |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 18.55 | Due to tripping of associated transmission lines |
|  |  | 26.07.09 | 16.02 | 28.07.09 | 20.05 | Condenser Tube Leakage |
|  |  | 29.07.09 | 12.12. | 29.07.09 | 12.55 | Auxiliary supply failure |
|  |  | 31.07.09 | 07.35 | 31.07.09 | 08.35 | Fire out |
|  |  | 06.08.09 | 20.48 | 11.08.09 | 08.30 | Condenser Tube Leakage |
|  |  | 11.08.09 | 08.35 | 11.08.09 | 09.08 | Low Vacuum |
|  |  | 15.08.09 | 05.02 | 15.08.09 | 17.10 | Maintenance work |
|  |  | 17.08.09 | 11.28 | 19.08.09 | 18.50 | Problem in coal bunker |
|  |  | 21.08.09 | 13.27 | 21.08.09 | 13.55 | Tripped due to jerk |
|  |  | 23.08.09 | 21.01 | 29.08.09 | 22.50 | Shortage of DM Water |
|  |  | 03.09.09 | 17.46 | 09.09.09 | 07.52 | Vapour Fan5-1 & Mill 5-2 out |
|  |  | 09.09.09 | 13.40 | 13.09.09 | 13.15 | Low vacuum |
|  |  | 17.09.09 | 12.45 | 17.09.09 | 18.25 | Low vacuum |
|  |  | 19.09.09 | 18.22 | 19.09.09 | 19.20 | Low vacuum |
|  |  | 20.09.09 | 12.42 | 27.09.09 | 12.47 | Coal Mill Problem |
|  |  | 28.09.09 | 02.50 | 03.10.09 | 03.05 | Boiler Tube Leakage |
|  |  | 03.10.09 | 18.09 | 31.10.09 | 18.50 | Due to tripping of 33kV Bay-38 |
|  |  | 04.10.09 | 22.58 | 12.10.09 | 13.55 | Boiler Tube Leakage |
|  |  | 14.10.09 | 20.00 | 16.10.00 | 14.20 | Boiler Tube Leakage |
|  |  | 17.10.09 | 21.55 | 18.10.09 | 06.35 | Coal not available |
|  |  | 22.10.09 | 09.45 | 01.11.09 | 03.20 | Boiler Tube Leakage |
|  |  | 02.11.09 | 17.40 | 23.11.09 | 16.10 | No coal availability |
|  |  | 24.11.09 | 02.05 |  |  | Unit stopped |

(B)  	RPH STATION

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 67.5 | 05.04.09 | 07.05 | 05.04.09 | 08.05 | Bus Bar Protection Operated |
|  |  | 10.04.09 | 08.48 | 10.04.09 | 19.33 | Condenser Tube Leakage |
|  |  | 09.05.09 | 03.16 | 09.05.09 | 09.46 | Cooling Line Problem |
|  |  | 12.05.09 | 20.05 | 13.05.09 | 14.26 | Turbine Vibration High |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 10.02 | Tripped due to tripping of associated transmission lines |
|  |  | 01.06.09 | 09.24 | 01.06.09 | 10.35 |  |
|  |  | 05.06.09 | 15.10 | 05.06.09 | 17.16 |  |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 15.20 |  |
|  |  | 29.06.09 | 15.40 | 29.06.09 | 20.50 |  |
|  |  | 03.07.09 | 01.20 | 06.07.09 | 14.20 | Thrust bearing maintenance. |
|  |  | 06.07.09 | 23.33 | 07.07.09 | 15.22 | Condenser Vacuum low |
|  |  | 07.07.09 | 20.09 | 07.07.09 | 20.42 | Flam failure |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 14.48 | Tripped due to tripping of associated transmission lines |
|  |  | 15.07.09 | 22.30 | 18.07.09 | 11.05 | Condenser Tube Leakage |
|  |  | 18.07.09 | 11.20 | 18.07.09 | 12.05 | Boiler Flame Failure |
|  |  | 28.07.09 | 15.27 | 28.07.09 | 16.22 | Flame Failure |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 67.5 | 28.07.09 | 18.03 | 28.07.09 | 18.39 | Flame Failure |
|  |  | 30.07.09 | 10.52 | 31.07.09 | 11.40 | Condenser Tube Leakage |
|  |  | 31.07.09 | 12.32 | 31.07.09 | 13.15 | Drum level high |
|  |  | 01.08.09 | 07.52 | 01.08.09 | 08.55 | Jerk due to appearance of money in yard |
|  |  | 01.08.09 | 18.20 | 01.08.09 | 19.01 | Flame failure |
|  |  | 02.08.09 | 15.19 | 02.08.09 | 15.45 | Flame failure |
|  |  | 07.08.09 | 10.44 | 07.08.09 | 11..31 | Flame failure |
|  |  | 09.08.09 | 03.55 | 09.08.09 | 04.25 | Flame failure |
|  |  | 21.08.09 | 14.34 | 21.08.09 | 18.00 | Buchloz Relay operated |
|  |  | 23.08.09 | 19.31 | 23.08.09 | 20.07 | Burner Pressure High |
|  |  | 25.08.09 | 17.50 | 25.08.09 | 18.25 | High Furnace pressure. |
|  |  | 27.08.09 | 17.35 | 27.08.09 | 20.30 | Boiler flame failure |
|  |  | 01.09.09 | 05.26 | 01.09.09 | 06.18 | Flame failure |
|  |  | 01.09.09 | 10.17 | 02.09.09 | 11.48 | Tripped due to tripping of associated transmission lines |
|  |  | 06.09.09 | 18.35 | 06.09.09 | 18.58 | Flame failure |
|  |  | 11.09.09 | 04.38 | 11.09.09 | 05.05 | Flame failure |
|  |  | 11.09.09 | 23.50 | 13.09.09 | 18.08 | Boiler Tube Leakage |
|  |  | 13.09.09 | 19.51 | 13.09.09 | 22.32 | Unit Auxiliary TX. tripped on E/F |
|  |  | 14.09.09 | 06.58 | 14.09.09 | 07.50 | Flame failure |
|  |  | 16.09.09 | 05.24 | 16.09.09 | 05.59 | Flame failure |
|  |  | 02.10.09 | 09.43 | 03.10.09 | 10.09 | To attend various leakages |
|  |  | 03.10.09 | 10.58 | 03.10.09 | 11.14 | Flame failure |
|  |  | 10.10.09 | 17.03 | 11.10.09 | 02.35 | To attend raw water |
|  |  | 02.11.09 | 22.24 | 02.11.09 | 23.01 | Control supply fail |
|  |  | 11.11.09 | 20.00 | 13.11.09 | 13.58 | Condenser Tube Leakage |
|  |  | 25.11.09 | 21.30 | 25.11.09 | 23.00 | To attend diesel generator set |
|  |  | 04.12.09 | 09.30 | 04.12.09 | 10.07 | Flame failure |
|  |  | 09.12.09 | 16.23 | 09.12.09 | 17.23 | Turbine Trip |
|  |  | 10.12.09 | 02.25 | 10.12.09 | 02.50 | Turbine Trip |
|  |  | 10.12.09 | 08.35 | 12.12.09 | 00.46 | Boiler Tube Leakage |
|  |  | 16.12.09 | 10.16 | 16.12.09 | 11.23 | Turbine Trip |
|  |  | 23.12.09 | 04.50 | 23.12.09 | 13.56 | Turbine Trip |
|  |  | 26.12.09 | 10.45 | 26.12.09 | 11.45 | Drum level low |
|  |  | 29.12.09 | 13.16 | 29.12.09 | 14.35 | Drum level low. |
|  |  | 02.01.10 | 04.18 | 03.01.10 | 00.35 | Due to tripping of transmission lines in Northern Region due to fog |
|  |  | 03.01.10 | 01.35 | 03.01.10 | 20.00 | Flame failure |
|  |  | 04.01.10 | 14.12 | 10.01.10 | 21.57 | Due to shut-down of 220kV IP – RPH Ckt-I & II |
|  |  | 11.01.10 | 15.58 | 14.01.10 | 00.23 | Due to tripping of transmission lines. Later taken on shut-down |
|  |  | 25.01.10 | 08.21 | 25.01.10 | 08.50 | Boiler tripped |
|  |  | 29.01.10 | 02.54 | 29.01.10 | 16.34 | Boiler drum level high |
|  |  | 31.01.10 | 16.28 | 31.01.10 | 17.23 | Tripped due to jerk |
|  |  | 03.02.10 | 21.13 | 0302.10 | 21.43 | Electrical Problem |
|  |  | 06.02.10 | 10.38 | 06.02.10 | 12.16 | Tripped along with tripping of associated transmission lines |
|  |  | 06.02.10 | 16.44 | 06.02.10 | 17.57 | Electrical fault |
|  |  | 09.02.10 | 08.14 | 09.02.10 | 08.35 | Boiler Flame Failure |
|  |  | 10.02.10 | 12.45 | 10.02.10 | 16.44 | Due to jerk |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 67.5 | 12.02.10 | 17.28 | 12.02.10 | 18.47 | Electrical problem |
|  |  | 13.02.10 | 06.22 | 14.02.10 | 06.50 | Flame failure |
|  |  | 14.02.10 | 17.37 | 14.02.10 | 18.45 | Tripped along with tripping of associated transmission lines |
|  |  | 19.02.10 | 17.05 | 19.02.10 | 17.23 | Cooling pump tripped |
|  |  | 20.02.10 | 06.32 | 22.02.10 | 22.25 | Maintenance work of cooling line |
| 2 | 67.5 | 05.04.09 | 07.05 | 05.04.09 | 08.05 | Bus Bar Protection Operated |
|  |  | 09.04.09 | 02.26 | 09.04.09 | 23.20 | Boiler Tube Leakage |
|  |  | 25.04.09 | 19.30 | 25.04.09 | 21.52 | Shaft Vibration High |
|  |  | 08.05.09 | 08.54 | 09.05.09 | 10.05 | Condenser Tube Leakage |
|  |  | 11.05.09 | 20.49 | 11.05.09 | 22.10 | Turbine Vibration high |
|  |  | 20.05.09 | 10.04 | 20.05.09 | 12.05 | Turbine Vibration high |
|  |  | 22.05.09 | 14.39 | 23.05.09 | 00.41 | Tripped due to tripping of associated transmission lines |
|  |  | 01.06.09 | 09.24 | 01.06.09 | 11.10 |  |
|  |  | 01.06.09 | 11.42 | 01.06.09 | 13.20 | Low vacuum |
|  |  | 05.06.09 | 15.10 | 05.06.09 | 17.45 | Tripped due to tripping of associated transmission lines |
|  |  | 07.06.09 | 07.25 | 07.06.09 | 21.06 | To check Turbine in Auxiliary |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 15.27 | Tripped due to tripping of associated transmission lines |
|  |  | 06.07.09 | 23.34 | 07.07.09 | 15.20 | Condenser Vacuum low |
|  |  | 10.07.09 | 22.08 | 10.07.09 | 23.08 | Condenser Vacuum low |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 15.20 | Tripped due to tripping of associated transmission lines |
|  |  | 18.07.09 | 20.20 | 19.07.09 | 11.45 | Electrical Fault |
|  |  | 01.08.09 | 01.15 | 03.08.09 | 05.58 | Condenser Tube Leakage |
|  |  | 21.08.09 | 16.28 | 21.08.09 | 18.54 | Furnace Pressure High |
|  |  | 27.08.09 | 17.51 | 27.08.9 | 22.08 | Tripped due to tripping of associated transmission lines |
|  |  | 28.08.09 | 00.18 | 28.08.09 | 01.33 | Turbine Tripped |
|  |  | 28.08.09 | 03.16 | 28.08.09 | 04.33 | Turbine Tripped |
|  |  | 28.08.09 | 03.57 | 29.08.09 | 04.15 | Turbine Tripped |
|  |  | 29.08.09 | 12.25 | 30.08.09 | 00.38 | Condenser Tube Leakage |
|  |  | 31.08.09 | 18.03 | 31.08.09 | 19.07 | Low Vacuum |
|  |  | 02.09.09 | 10.17 | 02.09.09 | 11.52 | Tripped due to tripping of associated transmission lines |
|  |  | 10.09.09 | 08.23 | 10.09.09 | 17.20 | Stator Earth Fault |
|  |  | 12.09.09 | 16.10 | 30.11.09 | 08.24 | For major overhauling |
|  |  | 30.11.09 | 14.36 | 30.11.09 | 19.41 | Shaft vibration high |
|  |  | 01.12.09 | 00.08 | 01.12.09 | 04.20 | Turbine problem |
|  |  | 01.12.09 | 21.14 | 01.12.09 | 22.56 | Drum level low |
|  |  | 05.12.09 | 15.30 | 05.12.09 | 17.59 | Turbine failure |
|  |  | 06.12.09 | 18.35 | 06.12.09 | 20.05 | Turbine failure |
|  |  | 11.12.09 | 06.24 | 11.12.09 | 07.26 | Turbine failure |
|  |  | 14.12.09 | 15.52 | 18.12.09 | 15.07 | Boiler Tube Leakage |
|  |  | 18.12.09 | 21.05 | 22.12.09 | 20.32 | Boiler Tube Leakage |
|  |  | 02.01.10 | 04.18 | 04.01.10 | 20.00 | Due to tripping of transmission lines in Northern Region due to fog |
|  |  | 04.01.10 | 14.12 | 11.01.10 | 02.00 | Due to Shut-down of 220kV IP – RPH Ckt-I & II |
|  |  | 11.01.10 | 15.58 | 11.01.10 | 17.35 | Tripped due to tripping of associated transmission lines |
|  |  | 11.01.10 | 18.04 | 28.02.10 | 11.35 | Turbine Vibration high |

(C)	Gas Turbine

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 30 | 15.04.09 | 16.15 | 16.04.09 | 22.55 | Due to overloading on 100 MVA Tr |
|  |  | 05.05.09 | 08.01 | 05.05.09 | 13.00 |  |
|  |  | 05.05.09 | 13.00 | 05.05.09 | 19.45 | For installing the ABT Meter. |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 15.44 | FSNL due to tripping of 160 MVA Tx at both end |
|  |  | 28.06.09 | 06.02 | 29.06.9 | 00.28 | To attend HSD leakag from the Nozzles. |
|  |  | 08.07.09 | 23.54 | 09.07.09 | 02.07 | Due to combined cycle trip alarm. |
|  |  | 09.07.09 | 11.40 | 17.07.09 | 08.55 | To attend the GT duct for HRSG# 1. |
|  |  | 17.07.09 | 13.16 | 17.07.09 | 16.14 | Emergency manual trip alarm |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 07.20 | Tripped due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 21.08.09 | 16.49 | 21.08.09 | 18.11 | SF6 gas pressure low |
|  |  | 23.08.09 | 06.05 | 23.08.09 | 21.10 | Gas Restriction |
|  |  | 28.08.09 | 04.32 | 28.08.09 | 05.45 | Exhaust Temperature High |
|  |  | 01.09.09 | 22.35 | 02.09.09 | 03.25 | Electrical Problem |
|  |  | 13.09.09 | 11.35 | 13.09.09 | 18.25 | To charge 66KV Dead Bus from Grid. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 16.50 | Tripped due to Grid failure. |
|  |  | 17.09.09 | 19.40 | 17.09.09 | 22.55 | Gas restriction |
|  |  | 20.09.09 | 06.02 | 20.09.09 | 09.45 | Gas restriction |
|  |  | 23.09.09 | 06.27 | 23.09.09 | 08.02 | Loss of flame. |
|  |  | 23.09.09 | 16.15 | 24.09.09 | 00.05 | To repair liquid fuel pump |
|  |  | 24.09.09 | 11.30 | 24.09.09 | 20.10 | To replace liquid fuel pump. |
|  |  | 26.09.09 | 08.05 | 26.09.09 | 08.10 | Came on FSNL due to jerk |
|  |  | 26.09.09 | 22.15 | 26.09.09 | 23.13 | High Exhaust Temperature |
|  |  | 30.09.09 | 11.47 | 30.09.09 | 13.55 | Tripped on gen. over current alarm |
|  |  | 09.10.09 | 22.40 | 10.10.09 | 02.50 | Generator O/C, Over voltage alarm appeared on protection panel. |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 15.30 | Tripped due to Grid Failure |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.28 | Failure of supply to HSD pump. |
|  |  | 17.11.09 | 14.15 | 18.11.09 | 17.58 | Gas restriction |
|  |  | 01.12.09 | 18.15 | 10.12.09 | 14.15 | Available on liquid fuel |
|  |  | 11.12.09 | 13.37 | 11.12.09 | 14.15 | Tripped on high TAD |
|  |  | 11.01.10 | 23.02 | 12.01.10 | 07.00 | Stopped due to swapping of gas to PPCL |
|  |  | 12.01.10 | 07.00 | 12.01.10 | 16.45 | Problem in DG set |
|  |  | 12.01.10 | 17.17 | 20.01.10 | 18.31 | Tripped on high Exhaust temperature |
|  |  | 21.01.10 | 07.35 | 21.01.10 | 08.27 | Tripped on loss of flame |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 17.19 | Came on FSNL due to tripping of 160 MVA Transformer |
|  |  | 31.01.10 | 09.05 | 01.02.10 | 04.05 | Available on Open Cycle |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.44 | Due to tripping of 100MVA & 160MVA Tx on jerk |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 14.48 | Bus Bar differential operation |
| 2 | 30 | 02.04.09 | 12.47 | 03.04.09 | 05.55 | Gas Restriction |
|  |  | 08.04.09 | 12.02 | 30.04.09 | 24.00 | Major Overhauling |
|  |  | 01.05.09 | 00.00 | 19.05.09 | 13.35 | Stopped for Major Inspection. |
|  |  | 22.05.09 | 20.10 | 23.05.09 | 21.50 | Swapping of gas to PPCL |
|  |  | 24.05.09 | 11.05 | 26.05.09 | 14.20 | Available on Open Cycle |
|  |  | 28.05.09 | 01.05 | 28.05.09 | 11.38 | Gas Restriction |
|  |  | 28.05.09 | 12.00 | 28.05.09 | 13.14 | Gas Restriction |
|  |  | 30.0.09 | 12.55 | 30.05.09 | 19.58 | Gas Restriction |
|  |  | 30.05.09 | 22.32 | 31.05.09 | 23.59 | Gas Restriction |
|  |  | 01.06.09 | 00.00 | 01.06.09 | 19.42 | Gas Restriction |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 30 | 03.06.09 | 05.50 | 03.06.09 | 17.14 | Gas Restriction |
|  |  | 04.06.09 | 06.32 | 04.06.09 | 09.35 | Gas Restriction |
|  |  | 05.06.09 | 11.30 | 05.06.09 | 19.35 | Gas Restriction |
|  |  | 07.06.09 | 01.48 | 07.06.09 | 18.45 | Gas Restriction |
|  |  | 08.06.09 | 00.10 | 08.06.09 | 18.20 | To attending Leakages |
|  |  | 09.06.09 | 00.02 | 09.06.09 | 10.35 | To attending Leakages |
|  |  | 10.06.09 | 07.09 | 10.06.09 | 17.50 | To attending Leakages |
|  |  | 11.06.09 | 07.47 | 11.06.09 | 19.55 | To attending Leakages |
|  |  | 12.06.09 | 03.02 | 15.06.09 | 19.20 | Swapping of gas to PPCL |
|  |  | 16.06.09 | 06.02 | 16.06.09 | 15.25 | Swapping of gas to PPCL |
|  |  | 16.06.09 | 15.55 | 16.06.09 | 20.45 | Exhaust Temperature high |
|  |  | 16.06.09 | 20.45 | 17.06.09 | 01.20 | Gas Restriction |
|  |  | 17.06.09 | 01.32 | 17.06.09 | 10.27 | Exhaust Temperature high |
|  |  | 17.06.09 | 11.30 | 17.06.09 | 14.32 | Gas Restriction |
|  |  | 18.06.09 | 00.02 | 21.06.09 | 11.20 | Swapping of gas to PPCL |
|  |  | 24.06.09 | 00.32 | 25.06.09 | 09.50 | Swapping of gas to PPCL |
|  |  | 26.06.09 | 22.25 | 26.06.09 | 22.55 | Exhaust Temperature high |
|  |  | 30.06.09 | 20.20 | 02.07 | 14.05 | Gas Restriction |
|  |  | 02.07.09 | 18.32 | 03.07.09 | 03.15 | Gas Restriction |
|  |  | 03.07.09 | 18.02 | 03.07.09 | 23.50 | Gas Restriction |
|  |  | 04.07.09 | 01.05 | 04.07.09 | 16.10 | Gas Restriction |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 06.38 | Due to blast in the breaker of 5 MVA in switch gear room. |
|  |  | 22.07.09 | 04.04 | 23.07.09 | 13.20 | To attend lube oil leakages. |
|  |  | 04.08.09 | 07.25 | 04.08.09 | 08.13 | Tripped while changing over from Gas to liquid fuel as the Distilite fuel pump-1 did not start on Auto. |
|  |  | 05.08.09 | 15.04 | 05.08.09 | 15.40 | Exhaust Temperature High |
|  |  | 23.08.09 | 21.15 | 23.08.09 | 23.11 | Gas Restriction |
|  |  | 23.08.09 | 23.11 | 20.09.09 | 00.52 | High vibration at 1800 RPM |
|  |  | 03.10.09 | 06.02 | 03.10.09 | 09.40 | Turbine under speed alarm appeared |
|  |  | 04.10.09 | 01.53 | 04.10.09 | 05.55 | Exhaust Temperature High |
|  |  | 07.10.09 | 20.38 | 08.10.09 | 16.10 | Gas Restriction |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.29 | Tripped due to Grid Failure |
|  |  | 04.11.09 | 14.16 | 04.11.09 | 16.25 | Stopped due GAD running high |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.35 | Failure of supply to HSD pump |
|  |  | 19.11.09 | 04.32 | 19.11.09 | 15.40 | Gas fuel Pressure low. |
|  |  | 23.11.09 | 00.43 | 23.11.09 | 03.38 | Low lube oil pressure |
|  |  | 30.11.09 | 19.05 | 12.12.09 | 11.35 | Available on liquid fuel |
|  |  | 19.12.09 | 11.05 | 22.12.09 | 19.25 |  |
|  |  | 23.12.09 | 20.45 | 23.12.09 | 22.45 |  |
|  |  | 02.01.10 | 14.07 | 02.01.10 | 14.40 | Exhaust temperature high |
|  |  | 05.01.20 | 17.45 | 05.01.10 | 18.10 | Exhaust temperature high |
|  |  | 05.01.10 | 19.25 | 06.01.10 | 16.01 | To attend IGV & Bleed valve problem |
|  |  | 11.01.10 | 07.28 | 11.01.10 | 07.50 | Exhaust temperature high |
|  |  | 15.01.10 | 14.50 | 16.01.10 | 06.50 | Swapping of gas to PPCL |
|  |  | 16.01.10 | 12.10 | 17.01.10 | 07.05 | Swapping of gas to PPCL |
|  |  | 23.01.10 | 05.58 | 23.01.10 | 15.50 | Stopped due to overloading of 100 MVA transformer-I as the 160 MVA Transformer was under shut down |
|  |  | 23.01.10 | 16.31 | 26.01.10 | 02.40 | Tripped on Exhaust temperature high |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 30 | 29.01.10 | 14.55 | 29.01.10 | 16.18 | Tripped on lube oil temp.high. |
|  |  | 31.01.10 | 09.05 | 31.01.10 | 19.05 | Available on liquid fuel |
|  |  | 05.02.10 | 15.15 | 05.02.10 | 16.14 | Due to tripping of 100MVA & 160MVA Tx on jerk |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 12.18 | High LTTH |
|  |  | 07.02.10 | 14.05 | 08.02.10 | 00.40 | Available on Open Cycle |
|  |  | 21.02.10 | 07.05 | 21.02.10 | 19.55 | Available on Open Cycle |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 14.46 | Bus Bar differential operation |
| 3 | 30 | 29.04.09 | 00.50 | 29.04.09 | 03.29 | LTTH High |
|  |  | 07.05.09 | 09.02 | 07.05.09 | 22.23 | Swapping of gas to PPCL |
|  |  | 17.05.09 | 12.42 | 17.05.09 | 17.42 | Lube oil temperature high |
|  |  | 19.05.09 | 12.45 | 22.05.09 | 19.40 | Swapping of gas to PPCL |
|  |  | 02.06.09 | 00.25 | 02.06.09 | 19.28 | Swapping of gas to PPCL |
|  |  | 09.06.09 | 23.02 | 10.06.09 | 06.52 | Swapping of gas to PPCL |
|  |  | 12.06.09 | 00.00 | 12.06.09 | 12.13 | Swapping of gas to PPCL |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 20.07 | Due to tripping of 160 MVA Tx at both end |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 14.45 |  |
|  |  | 16.06.09 | 19.10 | 17.06.09 | 09.45 | Swapping of gas to PPCL |
|  |  | 17.06.09 | 19.45 | 18.06.09 | 12.55 | Swapping of gas to PPCL |
|  |  | 21.06.09 | 12.30 | 22.06.09 | 00.28 | Swapping of gas to PPCL |
|  |  | 22.06.09 | 03.00 | 22.06.09 | 09.57 | Swapping of gas to PPCL |
|  |  | 22.06.09 | 22.15 | 23.06.09 | 12.40 | Swapping of gas to PPCL |
|  |  | 29.06.09 | 11.45 | 29.06.09 | 19.27 | To attend leakage in HRSG#3 |
|  |  | 30.06.09 | 01.32 | 30.06.09 | 11.55 | Swapping of gas to PPCL |
|  |  | 30.06.09 | 23.30 | 01.07.09 | 05.58 | Swapping of gas to PPCL |
|  |  | 07.07.09 | 05.42 | 07.07.09 | 13.47 | Malfunctioning of Battery Charger. |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 08.50 | Due to blast in the breaker of 5 MVA in switch gear room. |
|  |  | 27.07.09 | 20.50 | 27.07.09 | 23.07 | Tripped on loss of flame. |
|  |  | 15.08.09 | 10.15 | 15.08.09 | 20.55 | Gas Restriction |
|  |  | 21.08.09 | 14.38 | 21.08.09 | 16.58 | Loss of flame |
|  |  | 31.08.09 | 21.50 | 31.08.09 | 23.59 | Tripped without any Audio alarm. |
|  |  | 13.09.09 | 09.50 | 13.09.09 | 10.41 | Tripped due to Grid failure. |
|  |  | 13.09.09 | 11.20 | 13.09.09 | 16.15 | To charge 66 KV Dead Bus from Grid. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.20 | Tripped due to Grid failure. |
|  |  | 20.09.09 | 09.55 | 21.09.09 | 23.34 | To provide shut down on 160MVA Tx |
|  |  | 13.10.09 | 00.05 | 13.10.09 | 18.40 | Gas restriction |
|  |  | 13.10.09 | 20.05 | 14.10.09 | 20.10 |  |
|  |  | 14.10.09 | 22.05 | 15.10.09 | 18.02 |  |
|  |  | 16.10.09 | 22.03 | 17.10.09 | 18.02 |  |
|  |  | 17.10.09 | 20.08 | 18.10.09 | 18.02 |  |
|  |  | 18.10.09 | 20.05 | 19.10.09 | 18.45 |  |
|  |  | 19.10.09 | 20.05 | 20.10.09 | 18.05 |  |
|  |  | 21.10.09 | 00.01 | 21.10.09 | 18.00 |  |
|  |  | 21.10.09 | 20.05 | 22.10.09 | 17.45 |  |
|  |  | 23.10.09 | 06.10 | 23.10.09 | 11.28 |  |
|  |  | 29.10.09 | 21.02 | 29.10.09 | 23.50 |  |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 15.58 | Tripped due to Grid Failure |
|  |  | 31.10.09 | 07.02 | 31.10.09 | 18.04 | Gas restriction |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 3 | 30 | 01.11.09 | 10.04 | 02.11.09 | 10.15 | Gas restriction |
|  |  | 05.11.09 | 14.05 | 05.11.09 | 14.56 | High LTTH |
|  |  | 05.11.09 | 18.54 | 06.11.09 | 09.40 | Gas restriction |
|  |  | 06.11.09 | 16.35 | 07.11.09 | 12.15 | Gas restriction |
|  |  | 08.11.09 | 00.10 | 08.11.09 | 14.59 | Gas restriction |
|  |  | 13.11.09 | 14.32 | 14.11.09 | 18.40 | Gas restriction |
|  |  | 20.11.09 | 01.46 | 20.11.09 | 18.40 | Gas restriction |
|  |  | 20.11.09 | 11.02 | 24.11.09 | 03.59 | Gas restriction |
|  |  | 05.12.09 | 12.32 | 05.12.09 | 16.51 | To replace Generator absolute filter. |
|  |  | 10.12.09 | 15.47 | 14.12.09 | 07.30 | Available on liquid fire |
|  |  | 14.12.09 | 15.05 | 14.12.09 | 21.20 |  |
|  |  | 15.12.09 | 00.16 | 15.12.09 | 07.45 | Available on liquid fire |
|  |  | 15.12.09 | 15.00 | 16.12.09 | 18.08 |  |
|  |  | 17.12.09 | 00.05 | 21.12.09 | 22.55 |  |
|  |  | 22.12.09 | 19.30 | 02.01.10 | 11.25 |  |
|  |  | 06.01.10 | 12.02 | 06.01.10 | 20.50 | Swapping of gas to PPCL |
|  |  | 07.01.10 | 23.42 | 09.01.10 | 23.15 | Tripped on rotating earth diode fault |
|  |  | 10.01.10 | 19.15 | 11.01.10 | 06.45 | Stopped as generation on liquid fuel is not required |
|  |  | 11.01.10 | 23.10 | 12.01.10 | 07.05 |  |
|  |  | 13.01.10 | 00.05 | 13.01.10 | 07.06 |  |
|  |  | 13.01.10 | 17.01 | 14.01.10 | 09.53 |  |
|  |  | 15.01.10 | 14.52 | 17.01.10 | 19.57 |  |
|  |  | 19.01.10 | 20.29 | 20.01.10 | 06.38 |  |
|  |  | 21.01.10 | 17.45 | 22.01.10 | 06.50 | Swapping of gas to PPCL |
|  |  | 22.01.10 | 16.12 | 23.01.10 | 05.55 | Due to tripping of 160MVA Tx. and after that not taken on load due to overloading of 100 MVA Tx. |
|  |  | 24.01.10 | 14.40 | 24.01.10 | 16.40 | Tripped on LTTH high |
|  |  | 25.01.10 | 19.02 | 26.01.10 | 14.33 | Electrical trouble |
|  |  | 26.01.10 | 14.35 | 27.01.10 | 01.28 | Electrical trouble |
|  |  | 28.01.10 | 06.10 | 28.01.10 | 06.45 | Tripped on high TAD |
|  |  | 05.02.10 | 07.46 | 05.02.10 | 15.52 | Tripped on loss of Excitation field |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.12 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 08.02.10 | 19.52 | 08.02.10 | 20.52 | Tripped on high TAD |
|  |  | 17.02.10 | 23.02 | 18.02.10 | 18.05 | Stopped to avoid overloading on 160 MVA tx. |
|  |  | 20.02.10 | 17.02 | 22.02.10 | 19.05 | Stopped as generation on liquid fuel is not required |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 16.07 | tripped on over speed |
| 4 | 30 | 10.04.09 | 11.32 | 10.04.09 | 15.20 | Gas Restriction |
|  |  | 08.05.09 | 09.10 | 09.05.09 | 01.20 | Swapping of gas to PPCL |
|  |  | 10.05.09 | 17.24 | 10.05.09 | 20.25 | High exhaust temperature |
|  |  | 13.05.09 | 22.10 | 13.05.09 | 23.59 | Swapping of gas to PPCL |
|  |  | 24.05.09 | 11.05 | 25.05.09 | 21.20 | Gas Restriction |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 08.42 | To close 66 KV Bus Coupler. |
|  |  | 13.06.09 | 06.10 | 13.06.09 | 18.20 | Swapping of gas to PPCL |
|  |  | 14.06.09 | 15.04 | 16.06.09 | 02.38 | Swapping of gas to PPCL |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 4 | 30 | 26.06.09 | 01.100 | 26.06.09 | 13.27 | Swapping of gas to PPCL |
|  |  | 04.07.09 | 16.25 | 05.07.09 | 20.02 | Swapping of gas to PPCL |
|  |  | 05.07.09 | 20.28 | 07.07.09 | 19.50 | Lube oil pressure low |
|  |  | 13.07.09 | 16.03 | 28.07.09 | 15.28 | High exhaust temperature |
|  |  | 11.08.09 | 13.55 | 11.08.09 | 18.50 | Electrical trouble |
|  |  | 21.08.09 | 16.39 | 21.08.09 | 18.37 | Electrical trouble |
|  |  | 21.08.09 | 18.40 | 21.08.09 | 22.15 | Electrical trouble |
|  |  | 10.09.09 | 16.25 | 10.09.09 | 18.57 | Came on FSNL & reverse power operated on protection panel. |
|  |  | 13.09.09 | 09.50 | 13.09.09 | 14.10 | Came on FSNL due to Grid failure |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.25 | Tripped due to Grid failure |
|  |  | 20.09.09 | 01.15 | 21.09.09 | 22.50 | Swapping of gas to PPCL. |
|  |  | 24.09.09 | 13.58 | 24.09.09 | 16.15 | To check load hunting |
|  |  | 27.09.09 | 20.10 | 29.09.09 | 11.07 | Swapping of gas to PPCL. |
|  |  | 29.09.09 | 11.41 | 29.09.09 | 12.40 | Gas fuel hydraulic trip pressure low |
|  |  | 29.09.09 | 13.33 | 29.09.09 | 16.10 | Gas fuel hydraulic trip pressure low |
|  |  | 04.10.09 | 13.40 | 07.10.09 | 19.20 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 09.10.09 | 14.26 | 09.10.09 | 19.02 |  |
|  |  | 10.10.09 | 11.05 | 10.10.09 | 19.12 |  |
|  |  | 11.10.09 | 03.50 | 11.10.09 | 18.25 |  |
|  |  | 15.10.09 | 20.40 | 16.10.09 | 18.50 |  |
|  |  | 22.10.09 | 07.05 | 22.10.09 | 17.55 |  |
|  |  | 23.10.09 | 06.15 | 23.10.09 | 09.50 |  |
|  |  | 24.10.09 | 08.09 | 24.10.09 | 10.55 |  |
|  |  | 25.10.09 | 07.20 | 25.10.09 | 18.02 |  |
|  |  | 25.10.09 | 21.47 | 26.10.09 | 09.45 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 25.10.09 | 21.47 | 26.10.09 | 09.45 |  |
|  |  | 27.10.09 | 08.02 | 27.10.09 | 21.08 |  |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.27 |  |
|  |  | 02.11.09 | 18.00 | 03.11.09 | 11.30 |  |
|  |  | 03.11.09 | 11.30 | 05.11.09 | 18.45 |  |
|  |  | 09.11.09 | 00.35 | 10.11.09 | 18.18 |  |
|  |  | 10.11.09 | 20.15 | 11.11.09 | 18.58 |  |
|  |  | 12.11.09 | 00.40 | 13.11.09 | 07.25 |  |
|  |  | 15.11.09 | 01.05 | 18.11.09 | 14.05 |  |
|  |  | 03.12.09 | 13.00 | 03.12.09 | 15.35 | Stopped to replace Generator absolute filter. |
|  |  | 12.12.09 | 11.50 | 14.12.09 | 07.37 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 14.12.09 | 15.05 | 14.12.09 | 21.10 |  |
|  |  | 15.12.09 | 00.20 | 15.12.09 | 07.20 |  |
|  |  | 15.12.09 | 15.00 | 16.12.09 | 17.42 |  |
|  |  | 17.12.09 | 00.07 | 19.12.09 | 07.40 |  |
|  |  | 23.12.09 | 22.50 | 24.12.09 | 18.45 |  |
|  |  | 25.12.09 | 01.25 | 25.12.09 | 07.05 |  |
|  |  | 02.01.10 | 19.05 | 04.01.10 | 00.45 |  |
|  |  | 04.01.10 | 06.30 | 04.01.10 | 10.55 | Due to swapping of gas to PPCL |
|  |  | 04.01.10 | 15.15 | 05.01.10 | 09.00 |  |
|  |  | 05.01.10 | 13.10 | 05.01.10 | 20.00 |  |
|  |  | 06.01.10 | 23.10 | 07.01.10 | 06.59 |  |
|  |  | 07.01.10 | 23.05 | 07.01.10 | 23.58 |  |
|  |  | 14.01.10 | 08.41 | 14.01.10 | 21.00 | Tripped on Generator under voltage alarm |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 4 | 30 | 22.01.10 | 16.12 | 22.01.10 | 17.21 | Due to tripping of 160 MVA Tx |
|  |  | 27.01.10 | 16.31 | 28.01.10 | 21.10 | Tripped on loss of flame |
|  |  | 04.02.10 | 00.05 | 05.02.10 | 14.10 | Stopped due to swapping of gas to PPCL |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.40 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 06.02.10 | 01.14 | 06.02.10 | 03.28 | Tripped on Gas fuel hydraulic trip pressure low |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 14.40 | Tripped due to failure of Auxiliary supply. |
|  |  | 18.02.10 | 06.15 | 18.02.10 | 07.54 | Stopped as open cycle generation is not required by SLDC |
|  |  | 24.02.10 | 14.43 | 28.02.10 | 23.59 | Tripped on Electrical trouble normal shut down. |
| 5 | 30 | 18.04.09 | 06.02 | 18.04.09 | 11.45 | HRSG Leakage |
|  |  | 24.04.09 | 08.02 | 24.04.09 | 19.30 | Due to planned shut-down of 220/66kV 160MVA Pr. Tr. |
|  |  | 26.04.09 | 09.35 | 26.04.09 | 21.18 |  |
|  |  | 09.05.09 | 00.56 | 09.05.09 | 17.25 | C&I Problem |
|  |  | 10.05.09 | 14.52 | 10.05.09 | 17.15 | High exhaust temp. |
|  |  | 31.05.09 | 08.32 | 31.05.09 | 12.38 | To close 66 KV Bus Coupler |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 15.10 | Due to tripping of 100 MVA Tx. |
|  |  | 16.07.09 | 11.45 | 16.07.09 | 23.05 | C&I problem |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 06.45 | Due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 10.09.09 | 20.05 | 10.09.09 | 21.07 | Swapping of gas to PPCL. |
|  |  | 12.09.09 | 13.17 | 13.09.09 | 11.53 | Swapping of gas to PPCL. |
|  |  | 15.09.09 | 10.32 | 16.09.09 | 10.52 | Swapping of gas to PPCL. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.00 | Swapping of gas to PPCL. |
|  |  | 09.10.09 | 11.10 | 09.10.09 | 18.25 | Hydraulic Protection Trouble and Lube oil header temperature low |
|  |  | 28.10.09 | 01.05 | 28.10.09 | 17.35 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.04 |  |
|  |  | 04.11.09 | 20.36 | 06.11.09 | 09.52 |  |
|  |  | 06.11.09 | 12.45 | 09.11.09 | 19.10 |  |
|  |  | 10.11.09 | 20.45 | 11.11.09 | 00.50 |  |
|  |  | 12.11.09 | 05.56 | 12.11.09 | 19.15 |  |
|  |  | 24.11.09 | 13.02 | 25.11.09 | 23.12 |  |
|  |  | 26.11.09 | 10.46 | 01.12.09 | 14.35 |  |
|  |  | 06.12.09 | 14.40 | 06.12.09 | 16.04 | Stopped to attend Mark-IV system |
|  |  | 21.12.09 | 12.45 | 23.12.09 | 23.40 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 25.12.09 | 09.05 | 01.01.10 | 10.55 |  |
|  |  | 04.01.10 | 00.10 | 05.01.10 | 09.01 | SF-6 pressure low alarm. |
|  |  | 09.01.10 | 18.50 | 10.01.10 | 07.00 | Stopped as generation on liquid fuel is not required |
|  |  | 10.01.10 | 19.02 | 11.01.10 | 07.05 |  |
|  |  | 13.01.10 | 00.07 | 13.01.10 | 07.05 | Swapping of gas to PPCL |
|  |  | 13.01.10 | 16.46 | 13.01.10 | 18.20 | Loss of flame |
|  |  | 13.01.10 | 18.20 | 14.01.10 | 06.54 | Not taken on load due to as the generation on liquid fuel is not required by SLDC |
|  |  | 16.01.10 | 11.35 | 16.01.10 | 15.45 | Electrical trouble |
|  |  | 17.01.10 | 02.38 | 17.01.10 | 03.25 | Tripped at high TAD |
|  |  | 18.01.10 | 05.01 | 28.02.10 | 23.59 | Loss of flame and high vibration |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 6 | 30 | 29.04.09 | 17.26 | 29.04.09 | 22.55 | Electrical Fault |
|  |  | 09.05.09 | 14.32 | 09.05.09 | 23.59 | To install ABT -complaint meters. |
|  |  | 10.05.09 | 15.35 | 10.05.09 | 16.43 | Tripped without out any alarm |
|  |  | 11.05.09 | 22.02 | 12.05.09 | 17.44 | Swapping of gas to PPCL |
|  |  | 16.05.09 | 00.32 | 16.05.09 | 13.46 | Swapping of gas to PPCL |
|  |  | 26.05.09 | 14.31 | 26.05.09 | 17.50 | To replace Gen. differential relay. |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 08.42 | To close 66 KV Bus Coupler. |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 14.10 | Due to tripping of 100 MVA Tx at both end. |
|  |  | 30.06.09 | 2330 | 01.07.09 | 06.42 | Swapping of gas to PPCL |
|  |  | 12.07.09 | 02.40 | 12.07.09 | 14.25 | Loss of Excitation |
|  |  | 19.07.09 | 13.28 | 19.07.09 | 13.50 | FSNL due to Gen. Over heating alarm appearing on protection panel |
|  |  | 19.07.09 | 17.50 | 19.07.09 | 18.35 |  |
|  |  | 29.07.09 | 15.40 | 29.07.09 | 20.25 | Electrical Problem |
|  |  | 21.08.09 | 16.37 | 22.08.09 | 19.40 | Tripped on preignition pressure p-2 high and Battery ground alarm |
|  |  | 04.09.09 | 18.15 | 06.09.09 | 15.55 | Gas Restriction |
|  |  | 10.09.09 | 20.15 | 11.09.09 | 19.20 | Lss of excitation. |
|  |  | 13.09.09 | 09.50 | 13.09.09 | 10.43 | Came on FSNl due to Grid failure |
|  |  | 16.09.09 | 06.04 | 16.09.09 | 15.20 | Gas Restriction |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.32 | Tripped due to failure of Grid |
|  |  | 17.09.09 | 22.20 | 17.09.09 | 23.40 | Loss of Excitation |
|  |  | 26.09.09 | 08.05 | 26.09.09 | 08.21 | Came on FSNL due to jerk |
|  |  | 28.09.09 | 18.55 | 29.09.09 | 12.05 | Gas Restriction |
|  |  | 13.10.09 | 00.06 | 13.10.09 | 15.15 | Gas Restriction |
|  |  | 14.10.09 | 23.46 | 15.10.09 | 06.10 | Gas Restriction |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 15.37 | Tripped due to Grid Failure |
|  |  | 03.11.09 | 16.13 | 04.11.09 | 15.18 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 12.11.09 | 06.32 | 14.11.09 | 00.02 |  |
|  |  | 14.11.09 | 05.58 | 15.11.09 | 22.05 |  |
|  |  | 16.11.09 | 12.05 | 23.11.09 | 00.05 |  |
|  |  | 23.11.09 | 14.35 | 30.11.09 | 11.50 |  |
|  |  | 24.12.09 | 00.40 | 24.12.09 | 16.05 | Swapping of gas to PPCL |
|  |  | 02.01.10 | 19.05 | 03.01.10 | 18.55 | Stopped due to swapping of gas to PPCL |
|  |  | 05.01.10 | 13.05 | 06.01.10 | 06.42 |  |
|  |  | 06.01.10 | 19.05 | 07.01.10 | 06.57 |  |
|  |  | 07.01.10 | 23.05 | 08.01.10 | 07.00 |  |
|  |  | 08.01.10 | 07.00 | 08.01.10 | 13.10 | Problem in Diesel Engine |
|  |  | 09.01.10 | 00.02 | 09.01.10 | 06.59 | Stopped due to swapping of gas to PPCL |
|  |  | 14.01.10 | 15.16 | 15.01.10 | 17.30 |  |
|  |  | 15.01.10 | 17.45 | 16.01.10 | 06.57 |  |
|  |  | 16.01.10 | 16.37 | 17.01.10 | 07.15 |  |
|  |  | 17.01.10 | 14.02 | 18.01.10 | 13.50 |  |
|  |  | 19.01.10 | 13.30 | 19.01.10 | 18.58 |  |
|  |  | 22.01.10 | 17.05 | 22.01.10 | 18.05 |  |
|  |  | 27.01.10 | 01.35 | 27.01.10 | 06.45 | Available on open cycle. |
|  |  | 05.02.10 | 15.15 | 05.02.10 | 16.51 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 09.02.10 | 11.55 | 10.02.10 | 01.48 | Stopped as open cycle generation is not required by SLDC |
|  |  | 24.02.10 | 00.00 | 24.02.10 | 17.6 | Tripped on bus bar differential relay operated. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG1 | 34 | 06.04.09 | 10.30 | 08.04.09 | 12.00 | BTL |
|  |  | 21.04.09 | 00.05 | 22.04.09 | 21.10 | Maintenance work |
|  |  | 28.04.09 | 08.33 | 29.04.09 | 16.20 | HRSG Leakage |
|  |  | 30.04.09 | 11.58 | 30.04.09 | 12.28 | AVR System Problem |
|  |  | 01.05.09 | 16.58 | 01.05.09 | 20.33 | Tripped due to CEP 1-A tripped. |
|  |  | 03.05.09 | 23.10 | 04.05.09 | 04.40 | Tripped due to disappearance of drum parameters |
|  |  | 05.05.09 | 08.01 | 06.05.09 | 01.05 | Stopped due to stopping of GT-1 since only HRSG-I in service. |
|  |  | 13.05.09 | 11.20 | 13.05.09 | 14.27 | Tripped while change over Auxiliary supply from 7.5 MVA to 20 MVA. |
|  |  | 13.05.09 | 18.06 | 13.05.09 | 19.40 | Tripped on false alarm of HRSG# I |
|  |  | 22.05.09 | 19.42 | 22.05.09 | 22.05 | Malfunctioning of parameters |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 21.28 | Failure of 800 KVA transformer. |
|  |  | 02.06.09 | 18.13 | 02.06.09 | 19.20 | Due to tripping of BFP-1A & HRSG# 1 & 2. |
|  |  | 06.06.09 | 22.02 | 07.06.09 | 23.40 | Stopped to attend various leakages. |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 16.53 | Due to tripping of 160 MVA Tx at both end |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 14.42 | Due to tripping of 100 MVA Tx. |
|  |  | 20.06.09 | 06.02 | 20.06.09 | 23.48 | Stopped to attend various leakages. |
|  |  | 26.06.09 | 04.05 | 26.06.09 | 04.25 | Tripped on low hot well level |
|  |  | 30.06.09 | 13.00 | 30.06.09 | 20.05 | To attend leakage at PRDS station |
|  |  | 09.07.09 | 04.45 | 09.07.09 | 08.20 | Due to malfunctioning of parameters |
|  |  | 14.07.09 | 00.05 | 17.07.09 | 17.25 | Toto attend tube leakage in HRSG#2 |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 07.58 | Due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 21.07.09 | 08.38 | 21.07.09 | 09.28 | Tripped due to tripping of 800 KVA transformer on instantaneous O/C |
|  |  | 28.07.09 | 18.05 | 28.07.09 | 18.26 | Due to tripping of 7.5 MVA Tx |
|  |  | 09.08.09 | 17.55 | 09.08.09 | 19.47 | Tripped due to alarm of GT-1 Tripped appeared on STG# I BCD which led to tripping of HRSG-I & subsequently STG# I. |
|  |  | 23.08.09 | 00.05 | 24.08.09 | 19.10 | To attend PRDS leakage. |
|  |  | 26.08.09 | 02.15 | 26.08.09 | 05.05 | Tripped due to Closing of MS-1 Valve |
|  |  | 26.08.09 | 18.05 | 26.08.09 | 19.52 | Channel-I & II operated. |
|  |  | 27.08.09 | 08.15 | 27.08.09 | 12.55 | Tripped though all the parameters were normal at BCD. |
|  |  | 27.08.09 | 15.05 | 27.08.09 | 20.50 | Control Oil pressure very low |
|  |  | 28.08.09 | 04.32 | 28.08.09 | 06.35 | Tripped due to tripping of GT# 1. |
|  |  | 01.09.09 | 22.35 | 02.09.09 | 04.55 | Tripped due to tripping of GT# 1 |
|  |  | 02.09.09 | 07.31 | 02.09.09 | 22.55 | C&I Problem |
|  |  | 07.09.09 | 02.20 | 07.09.09 | 20.04 | Tripped due to GT# 1came on FSNL |
|  |  | 13.09.09 | 09.50 | 14.09.09 | 06.40 | Tripped due to Grid failure. |
|  |  | 14.09.09 | 13.52 | 14.09.09 | 19.05 | Exhaust Steam Pressure High. |
|  |  | 17.09.09 | 10.54 | 18.09.09 | 00.20 | Tripped during Grid failure |
|  |  | 28.09.09 | 10.05 | 28.09.09 | 11.52 | Turbine shaft vibration very high. |
|  |  | 30.10.09 | 02.40 | 30.10.09 | 04.33 | Tripped due to failure of BK Card |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.25 | Tripped due to Grid Failure |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 21.20 | Due to tripping of GT-I & II |
|  |  | 09.11.09 | 22.25 | 10.11.09 | 02.46 | Due to choke of suction strainer of both BFPs. |
|  |  | 10.11.09 | 09.11 | 10.11.09 | 11.50 | Low Vacuum |
|  |  | 01.12.09 | 18.15 | 11.12.09 | 20.45 | Stopped for condenser cleaning |
|  |  | 14.12.09 | 00.15 | 14.12.09 | 03.35 | Channel-I& II operated |
|  |  | 19.12.09 | 05.06 | 19.12.09 | 05.58 |  |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG1 | 34 | 19.12.09 | 08.05 | 19.12.09 | 08.55 |  |
|  |  | 24.12.09 | 17.08 | 24.12.09 | 18.32 |  |
|  |  | 26.12.09 | 14.05 | 26.12.09 | 16.10 | Stopped to attend hot spot |
|  |  | 21.01.10 | 09.35 | 21.01.10 | 10.50 | tripped on Ch-I and II |
|  |  | 31.01.10 | 09.05 | 02.02.10 | 03.35 | Stopped to attend leakages in CPH |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.58 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 13.15 | Tripped due to failure of Auxiliary supply. |
|  |  | 06.02.10 | 19.40 | 06.02.10 | 20.20 | Failure of Auxiliary supply. |
|  |  | 15.02.10 | 17.26 | 15.02.10 | 18.10 | Tripped due to tripping of VB-II radial feeder relay 51& 64 operated. |
|  |  | 20.02.10 | 01.15 | 20.02.10 | 04.35 | Tripped as AOP-I tripped due to jerk in the control Room as VB-I tripped. |
|  |  | 20.02.10 | 16.43 | 20.02.10 | 17.15 | Control oil header pressure low. |
|  |  | 20.02.10 | 17.55 | 20.02.10 | 22.15 | Control oil header pressure low. |
|  |  | 21.02.10 | 06.40 | 21.02.10 | 20.05 | Stopped to install flow meter to measure DM Water and to arrend other leakages. |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 16.55 | Bus bar differential relay operated. |
|  |  | 25.02.10 | 13.15 | 25.02.10 | 14.20 | Tripped in the jerk due snapping of conductor of VB-II |
|  |  | 25.02.10 | 15.05 | 25.02.10 | 20.20 | Stopped to attend the frequent tripping of BFPs by C&I department |
| STG2 | 34 | 07.04.09 | 00.05 | 08.04.09 | 22.02 | To attend leakage |
|  |  | 10.04.09 | 02.02 | 10.04.09 | 02.40 | Class A relay group-2 operated |
|  |  | 30.04.09 | 11.58 | 30.04.09 | 12.28 | Class 'B' trip relay operated& 40G |
|  |  | 06.05.09 | 09.05 | 06.05.09 | 21.06 | To install ABT -complaint meters. |
|  |  | 13.05.09 | 11.20 | 13.05.09 | 11.40 | Tripped while change over of Auxiliary supply from 7.5 MVA to 20 MVA. |
|  |  | 29.05.09 | 19.24 | 29.05.09 | 20.20 | Tripped due to following relay i) Generator class-A group-II 86GA-2. |
|  |  | 29.05.09 | 20.31 | 29.05.09 | 21.55 |  |
|  |  | 31.05.09 | 07.37 | 31.05.09 | 09.55 | Due to tripping of 100 MVA Tx-II. |
|  |  | 02.06.09 | 17.09 | 02.06.09 | 19.05 | Due to tripping of HRSG# 4. |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 17.05 | Due to tripping of 100 MVA Tx. |
|  |  | 07.07.09 | 05.44 | 07.07.09 | 15.28 | Tripped due to tripping of GT# 3 |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 12.08 | Due to blast in the breaker of 5 MVA in switch gear room. |
|  |  | 21.07.09 | 08.38 | 21.07.09 | 09.18 | Tripped due to tripping of 800 KVA transformer on instantaneous O/C |
|  |  | 23.07.09 | 12.27 | 23.07.09 | 13.13 | Tripped without any abnormality of system. |
|  |  | 27.07.09 | 20.50 | 28.07.09 | 00.28 | Tripped due to tripping of GT# 3 which is tripped on loss of flame. |
|  |  | 28.07.09 | 18.05 | 28.07.09 | 18.20 | Due to tripping of 7.5 MVA Tx. |
|  |  | 31.07.09 | 13.32 | 31.07.09 | 19.15 | To attend the condensate water transfer problem from hot well to dearater. |
|  |  | 15.08.09 | 21.25 | 15.08.09 | 22.28 | Drum level very high. |
|  |  | 16.08.09 | 13.32 | 16.08.09 | 14.15 | Due to tripping of BFP-2B. |
|  |  | 21.08.09 | 16.39 | 21.08.09 | 17.52 | Due to tripping of GT#4. |
|  |  | 26.08.09 | 14.10 | 27.08.09 | 23.59 | Shortage of DM water |
|  |  | 13.09.09 | 09.50 | 13.09.08 | 17.55 | Tripped due to Grid failure. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 13.50 | Tripped due to Grid failure. |
|  |  | 20.09.09 | 09.55 | 22.09.09 | 11.05 | Swapping of gas to PPCL. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG2 | 34 | 21.10.09 | 10.02 | 23.10.09 | 14.29 | Parameter of HRSG-4 disappeared while resetting these, Boiler-4 tripped consequently STG tripped |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 21.25 | Tripped due to Grid Failure |
|  |  | 05.11.09 | 14.05 | 05.11.09 | 15.32 | Tripped due to tripping of GT# 3 |
|  |  | 05.11.09 | 17.31 | 05.11.09 | 19.55 | Stopped to attend leakages |
|  |  | 06.11.09 | 17.02 | 06.11.09 | 18.50 | To clean suction strainer of CEP |
|  |  | 07.11.09 | 17.01 | 07.11.09 | 20.10 | Stopped to attend leakages |
|  |  | 14.11.09 | 00.57 | 14.11.09 | 07.40 | Heavy leakage from flange of SRV |
|  |  | 21.11.09 | 05.17 | 21.11.09 | 21.45 | Due to failure of fuse of Power Distribution Module |
|  |  | 12.12.09 | 11.50 | 23.12.09 | 03.00 | Stopped for condenser cleaning |
|  |  | 23.12.09 | 02.02 | 23.12.09 | 18.30 | Exhaust steam pressure high. |
|  |  | 23.12.09 | 18.40 | 24.12.09 | 23.55 | Due to problem in governing system |
|  |  | 25.12.09 | 00.50 | 25.12.09 | 08.55 | Machine tripped due to load not increased |
|  |  | 04.01.10 | 06.45 | 04.01.10 | 07.58 | tripped due to field failure relay |
|  |  | 05.01.10 | 16.30 | 05.01.10 | 23.26 | tripped on Ch-I and II |
|  |  | 05.01.10 | 23.58 | 06.01.10 | 10.50 | Manually tripped as there was hunting in the load |
|  |  | 06.01.10 | 12.03 | 06.01.10 | 12.38 | tripped on Ch-I and II |
|  |  | 06.01.10 | 14.16 | 06.01.10 | 15.59 | Axial shift very high |
|  |  | 06.01.10 | 17.02 | 06.01.10 | 18.45 | Low vacuum |
|  |  | 07.01.10 | 23.42 | 08.01.10 | 00.28 | Tripped due to tripping of GT-3 |
|  |  | 10.01.10 | 11.44 | 10.01.10 | 12.18 | due to tripping of HRSG-4 and there rafter CEP-2A without any alarm |
|  |  | 11.01.10 | 15.45 | 11.01.10 | 18.25 | Stopped due to choking of CEPs. |
|  |  | 14.01.10 | 08.41 | 14.01.10 | 11.52 | Tripped due to tripping of GT-4 |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 18.31 | Due to tripping of 160 MVA Tx |
|  |  | 28.01.10 | 06.10 | 28.01.10 | 07.33 | High TAD |
|  |  | 31.01.10 | 15.48 | 31.01.10 | 16.55 | Low vacuum |
|  |  | 05.02.10 | 07.46 | 05.02.10 | 18.50 | Tripped due to tripping of GT#3 |
|  |  | 05.02.10 | 19.54 | 05.02.10 | 23.12 | Tripped on Ch-I and II. |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 14.30 | Tripped due to failure of Auxiliary supply. |
|  |  | 06.02.10 | 19.40 | 06.02.10 | 20.15 | Tripped due to failure of Auxiliary supply. |
|  |  | 18.02.10 | 06.15 | 18.02.10 | 19.55 | Stopped to attend various leakages |
|  |  | 22.02.10 | 11.18 | 22.02.10 | 12.05 | Tripped on Ch-I and II. |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 17.35 | Bus bar differential relay operated. |
| STG3 | 34 | 05.05.09 | 16.15 | 05.05.09 | 16.50 | To install ABT -complaint meters. |
|  |  | 09.05.09 | 09.02 | 09.05.09 | 21.25 | To attend leakages |
|  |  | 10.05.09 | 15.35 | 10.05.09 | 19.15 | Due to tripping of GT No. 6. |
|  |  | 11.05.09 | 17.42 | 11.05.09 | 18.35 | Tripped due to disappearance of hot well level parameters. |
|  |  | 13.05.09 | 11.20 | 13.05.09 | 12.40 | Tripped while change over of Auxiliary supply from 7.5 MVA to 20 MVA. |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 10.29 | Due to failure of 800 KVA Tx |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 18.20 | Tripped due to 160 MVA Tx at both end |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 16.12 | Due to tripping of 100 MVA Tx. |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 08.28 | Due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 21.07.09 | 08.38 | 21.07.09 | 09.35 | Tripped due to tripping of 800 KVA transformer on instantaneous O/C |
|  |  | 23.07.09 | 14.02 | 23.07.09 | 21.50 | Generator class -A relay operated. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG3 | 34 | 28.07.09 | 18.05 | 28.07.09 | 18.35 | Due to tripping of 7.5 MVA Tx. |
|  |  | 28.08.09 | 03.10 | 11.09.09 | 02.02 | Axial Shift Problem |
|  |  | 12.09.09 | 06.16 | 19.09.09 | 14.13 | Channel-I & II operated |
|  |  | 25.10.09 | 13.05 | 26.10.09 | 13.25 | Control oil header pressure low |
|  |  | 25.10.09 | 23.31 | 26.10.09 | 15.10 | Low vacuum |
|  |  | 27.10.09 | 17.37 | 27.10.09 | 18.40 | Low vacuum |
|  |  | 30.10.09 | 15.10 | 31.10.09 | 14.40 | Tripped due to Grid Failure |
|  |  | 02.11.09 | 11.57 | 03.11.09 | 00.10 | To attend leakages and Condenser back washing |
|  |  | 10.11.09 | 23.28 | 11.11.09 | 00.20 | Low Vacuum |
|  |  | 11.11.09 | 17.01 | 11.11.09 | 23.40 | To attend leakages |
|  |  | 12.11.09 | 00.45 | 12.11.09 | 23.50 | Exhaust Temperature High |
|  |  | 24.11.09 | 12.55 | 01.12.09 | 04.05 | Stopped for Condenser cleaning |
|  |  | 31.12.09 | 03.15 | 31.12.09 | 09.25 | Axial shift very high |
|  |  | 01.01.10 | 06.02 | 01.01.10 | 06.53 | Tripped on sudden throw off load and Class-A relay operated |
|  |  | 07.01.10 | 06.00 | 07.01.10 | 22.46 | Stopped to attend leakages |
|  |  | 17.01.10 | 02.38 | 17.01.10 | 04.05 | Tripped due to tripping of GT-5 |
|  |  | 18.01.10 | 05.01 | 18.01.10 | 17.20 | Tripped due to tripping of GT-5 |
|  |  | 19.1.10 | 13.28 | 19.01.10 | 21.32 | Stopped as GT-6 stopped by SLDC |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 20.20 | Due to tripping of 160 MVA Tx |
|  |  | 26.01.10 | 17.20 | 28.01.10 | 00.11 | Tripped on Generator Stator E/F |
|  |  | 03.02.10 | 19.10 | 03.02.10 | 21.42 | Manually tripped as BFP-3A was tripping frequently. |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 18.12 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 19.15 | Failure of Auxiliary supply. |
|  |  | 09.02.10 | 11.50 | 10.02.10 | 07.05 | Mechanical problem |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 19.05 | Bus bar differential relay operated. |
|  |  | 26.02.10 | 13.10 | 26.02.10 | 15.10 | Tripped due to Stand by Transformer earth fault relay. |

(D)   PRAGATI STATION

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
| 1 | 104 | Date | Time | Date | Time |  |
|  |  | 18.04.09 | 15.42 | 18.04.09 | 16.26 | Tripped due to jerk |
|  |  | 27.04.09 | 10.48 | 28.04.09 | 13.25 | Hydraulic Pressure Low |
|  |  | 19.05.09 | 20.55 | 19.05.09 | 22.17 | Tripped due to tripping of associated transmission lines |
|  |  | 25.05.09 | 21.29 | 25.05.09 | 22.56 | Tripped due to tripping of associated transmission lines |
|  |  | 05.06.09 | 02.48 | 05.06.09 | 10.07 |  |
|  |  | 03.07.09 | 07.28 | 03.07.09 | 12.27 |  |
|  |  | 04.07.09 | 11.42 | 04.07.09 | 12.01 |  |
|  |  | 06.07.09 | 14.10 | 06.07.09 | 14.28 |  |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 10.18 |  |
|  |  | 05.08.09 | 16.15 | 05.08.09 | 17.37 |  |
|  |  | 10.08.09 | 19.09 | 10.08.09 | 19.25 |  |
|  |  | 12.08.09 | 15.15 | 12.08.09 | 16.31 |  |
|  |  | 20.08.09 | 21.16 | 22.08.09 | 11.02 | Internal Fault |
|  |  | 22.08.09 | 18.17 | 22.08.09 | 20.10 | Internal Fault |
|  |  | 27.08.09 | 18.22 | 27.08.09 | 18.26 | Tripped due to tripping of associated transmission lines |
|  |  | 06.09.09 | 17.00 | 06.09.09 | 17.14 |  |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 104 | 13.09.09 | 09.52 | 13.09.09 | 12.00 | Tripped due to tripping of associated transmission lines |
|  |  | 17.09.09 | 10.57 | 17.09.09 | 11.50 |  |
|  |  | 22.09.09 | 10.45 | 22.09.09 | 14.56 | Internal Fault |
|  |  | 03.10.09 | 23.45 | 04.10.09 | 01.29 | Tripped due to tripping of associated transmission lines |
|  |  | 11.10.09 | 12.09 | 11.10.09 | 15.00 | Internal Fault |
|  |  | 23.10.09 | 00.00 | 30.10.09 | 18.35 | Maintenance Work |
|  |  | 31.10.09 | 12.22 | 31.10.09 | 13.50 | Tripped due to tripping of associated transmission lines |
|  |  | 04.11.09 | 08.55 | 04.11.09 | 15.48 |  |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.35 |  |
|  |  | 14.12.09 | 16.12 | 16.12.09 | 01.08 | Rotor tripped on E/F |
|  |  | 27.12.09 | 13.44 | 27.12.09 | 15.08 | Internal Fault |
|  |  | 02.01.10 | 04.14 | 04.01.10 | 05.10 | Tripping of lines in Northern Region due to fog |
|  |  | 02.01.10 | 05.40 | 02.01.10 | 08.30 |  |
|  |  | 02.01.10 | 21.45 | 02.01.10 | 23.05 |  |
|  |  | 11.01.10 | 15.59 | 11.01.10 | 16.47 |  |
|  |  | 22.01.10 | 13.30 | 22.01.10 | 16.05 | Bleed valve problem |
|  |  | 23.01.10 | 12.45 | 23.01.10 | 17.36 | To change the filter |
|  |  | 29.01.10 | 12.12 | 29.01.10 | 12.58 | Internal fault |
|  |  | 06.02.10 | 10.57 | 06.02.10 | 11.26 | Tripped due to tripping of associated transmission lines |
|  |  | 14.02.10 | 17.37 | 16.02.10 | 00.11 | Internal fault |
|  |  | 26.02.10 | 13.00 | 26.02.10 | 14.14 | Air inlet problem |
| 2 | 104 | 19.04.09 | 10.29 | 19.04.09 | 11.27 | Tripped due to tripping of associated transmission lines |
|  |  | 19.05.09 | 20.55 | 19.05.09 | 22.07 |  |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 14.28 |  |
|  |  | 22.05.09 | 15.36 | 22.05.09 | 15.51 | Tripped due to tripping of associated transmission lines |
|  |  | 01.06.09 | 09.26 | 01.06.09 | 09.52 |  |
|  |  | 04.06.09 | 00.00 | 05.06.09 | 05.26 | Shut-down |
|  |  | 05.06.09 | 15.06 | 05.06.09 | 17.21 | Tripped due to tripping of associated transmission lines |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 14.20 |  |
|  |  | 15.07.09 | 00.30 | 17.08.09 | 19.50 | Shut-down. |
|  |  | 17.08.09 | 23.54 | 18.08.09 | 04.00 | Tripped due to tripping of associated transmission lines |
|  |  | 21.08.09 | 14.42 | 21.08.09 | 15.27 |  |
|  |  | 27.08.09 | 17.53 | 27.08.09 | 19.18 |  |
|  |  | 01.09.09 | 05.05 | 01.09.09 | 05.52 |  |
|  |  | 02.09.09 | 10.17 | 02.09.09 | 11.41 |  |
|  |  | 08.09.09 | 12.05 | 08.09.09 | 13.25 | Internal fault |
|  |  | 13.09.09 | 09.52 | 13.09.09 | 11.26 | Tripped due to tripping of associated transmission lines |
|  |  | 13.09.09 | 18.30 | 13.09.09 | 19.52 | Internal fault |
|  |  | 17.09.09 | 10.57 | 17.09.09 | 12.34 | Tripped due to tripping of associated transmission lines |
|  |  | 18.09.09 | 02.47 | 18.09.09 | 04.20 |  |
|  |  | 19.09.09 | 10.22 | 19.09.09 | 11.26 |  |
|  |  | 28.09.09 | 07.39 | 28.09.09 | 08.30 |  |
|  |  | 02.10.09 | 10.29 | 02.10.09 | 12.21 |  |
|  |  | 11.10.09 | 12.07 | 11.10.09 | 13.38 | Internal Fault |
|  |  | 30.10.09 | 15.12 | 30.10.09 | 15.47 | Transient Fault |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.58 | Tripped due to tripping of associated transmission lines |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 104 | 16.11.09 | 18.14 | 16.11.09 | 19.30 |  |
|  |  | 14.01.10 | 17.13 | 15.01.10 | 11.16 | Internal fault |
|  |  | 05.02.10 | 16.02 | 05.02.10 | 18.00 | Tripped due to tripping of associated transmission lines |
|  |  | 16.02.10 | 10.46 | 18.02.10 | 18.14 | Shut-down for over-hauling of SF6 breaker at IP Ext. end. |
| STG | 122 | 07.04.09 | 06.34 | 07.04.09 | 07.45 | Tripped due to tripping of associated transmission lines |
|  |  | 19.04.09 | 10.29 | 19.04.09 | 12.41 |  |
|  |  | 26.04.09 | 07.11 | 28.04.09 | 13.25 |  |
|  |  | 16.05.09 | 18.44 | 16.05.09 | 20.24 |  |
|  |  | 19.05.09 | 20.55 | 19.05.09 | 23.20 |  |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 15.39 |  |
|  |  | 01.06.09 | 09.26 | 01.06.09 | 10.41 |  |
|  |  | 04.06.09 | 11.25 | 04.06.09 | 15.32 | Oil leakage from ESU |
|  |  | 05.06.09 | 15.06 | 05.06.09 | 16.40 | Tripped due to tripping of associated transmission lines |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 15.20 |  |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 10.42 |  |
|  |  | 15.07.09 | 11.56 | 15.07.09 | 12.50 | Problem in Boiler feed pump |
|  |  | 10.08.09 | 19.10 | 10.08.09 | 20.14 | Tripped due to tripping of associated transmission lines |
|  |  | 12.08.09 | 15.15 | 12.08.09 | 17.20 |  |
|  |  | 18.08.09 | 00.15 | 18.08.09 | 01.55 | Internal Fault |
|  |  | 21.08.09 | 14.43 | 21.08.09 | 16.17 | Tripped due to tripping of associated transmission lines |
|  |  | 27.08.09 | 17.53 | 27.08.09 | 20.20 |  |
|  |  | 11.10.09 | 12.07 | 11.10.09 | 15.06 | Internal Fault |
|  |  | 30.10.09 | 15.12 | 30.10.09 | 16.55 | Internal Fault |
|  |  | 02.01.10 | 04.14 | 02.01.10 | 07.52 | Tripping of lines in Northern Region due to fog |
|  |  | 02.01.10 | 21.45 | 03.01.10 | 00.01 |  |
|  |  | 11.01.10 | 15.59 | 11.01.10 | 16.39 |  |
|  |  | 26.01.10 | 17.56 | 28.01.10 | 16.51 | Excitation problem |
|  |  | 29.01.10 | 12.12 | 29.01.10 | 14.48 | Internal fault |
|  |  | 05.02.10 | 10.50 | 06.02.10 | 12.00 | Vibration in Generator Bearing |
|  |  | 06.02.10 | 10.37 | 06.02.10 | 12.48 | Tripped due to tripping of associated transmission lines |
|  |  | 09.02.10 | 12.55 | 09.02.10 | 14.08 | Internal fault |
|  |  | 14.02.10 | 17.37 | 14.02.10 | 20.09 | Tripped due to tripping of associated transmission lines |

(E)   	BADARPUR THERMAL POWER STATION

| Unit | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 95 | 30.07.09 | 06.45 | 14.09.09 | 17.00 | Planned shut-down for major overhauling |
|  |  | 22.09.09 | 21.14 | 23.09.09 | 04.08 | Vacuum problem |
|  |  | 23.09.09 | 04.15 | 23.09.09 | 07.02 | Vacuum problem |
|  |  | 26.09.09 | 17.18 | 27.09.09 | 10.40 | Drum main hole leakage |
| 2 | 95 | 10.05.09 | 13.12 | 10.05.09 | 15.15 | Bus differential operated |
|  |  | 16.07.09 | 17.42 | 18.07.09 | 05.25 | Boiler Tube Leakage |
|  |  | 29.07.09 | 17.56 | 30.07.09 | 22.30 | Furnace Failure |
|  |  | 11.08.09 | 21.29 | 11.08.09 | 22.50 | Furnace problem |
|  |  | 30.08.09 | 14.50 | 31.08.09 | 11.00 | DC Control failure |
|  |  | 22.10.09 | 21.48 | 28.12.09 | 05.16 | Annual maintenance |
|  |  | 11.02.10 | 20.10 | 12.02.10 | 08.40 | Reserver shut-down |
| 3 | 95 | 12.04.09 | 05.34 | 12.04.09 | 19.43 | Electrical problem |
|  |  | 13.04.09 | 17.22 | 13.04.09 | 20.45 | Electrical problem |
|  |  | 25.04.09 | 22.43 | 27.04.09 | 22.47 | Planned Shut-down |
|  |  | 26.05.09 | 20.54 | 27.05.09 | 17.45 | Boiler Tube Leakage |
|  |  | 01.09.09 | 08.40 | 02.09.09 | 15.37 | Boiler Tube Leakage |
|  |  | 30.10.09 | 11.15 | 30.10.09 | 13.04 | Auxiliary supply failed |
|  |  | 16.12.09 | 06.58 | 17.12.09 | 11.65 | Drum level low |
|  |  | 03.02.10 | 13.33 | 04.0210 | 14.05 | Boiler Tube Leakage |
|  |  | 26.02.10 | 2105 | 27.02.10 | 09.30 | Boiler Tube Leakage |
| 4 | 210 | 01.04.09 | 12.18 | 17.04.09 | 23.59 | Planned Shut-Down for over-hauling |
|  |  | 18.04.09 | 12.35 | 18.04.09 | 15.48 | Tripped along with tripping of 220kV BTPS – Noida Ckt. |
|  |  | 18.05.09 | 13.12 | 10.05.09 | 22.13 | Bus differential operated |
|  |  | 10.06.09 | 16.44 | 11.06.09 | 16.58 | Boiler Tube Leakage |
|  |  | 19.06.09 | 09.52 | 20.06.09 | 09.23 | Boiler Tube Leakage |
|  |  | 11.10.09 | 20.18 | 13.10.09 | 13.09.09 | Boiler Tube Leakage |
|  |  | 24.10.09 | 10.03 | 25.10.09 | 05.51 | Boiler Tube Leakage |
|  |  | 16.11.09 | 14.58 | 17.11.09 | 09.54 | Shut-down |
|  |  | 29.11.09 | 06.43 | 29.11.09 | 23.32 | Boiler Tube leakage |
|  |  | 05.12.09 | 04.54 | 05.12.09 | 12.04 | Electrical Problem |
|  |  | 12.12.09 | 19.25 | 14.12.09 | 16.25 | Boiler Tube leakage |
|  |  | 20.12.09 | 18.35 | 22.12.09 | 09.58 | Boiler Tube leakage |
|  |  | 26.01.10 | 00.05 | 27.01.10 | 09.38 | Reserve shut-down |
|  |  | 02.02.10 | 16.00 | 02.02.10 | 17.55 | Electrical fault |
|  |  | 24.02.10 | 07.22 | 26.02.10 | 08.35 | Boiler Tube Leakage |
| 5 | 210 | 07.08.09 | 17.43 | 07.08.09 | 19.40 | Furnace Protection. |
|  |  | 18.11.09 | 00.50 | 19.11.09 | 10.38 | Boiler Tube Leakage |
|  |  | 12.12.09 | 14.35 | 15.12.09 | 19.35 | Boiler Tube leakage |
|  |  | 01.01.10 | 13.08 | 03.01.10 | 07.15 | Boiler Tube leakage |
|  |  | 11.01.10 | 07.38 | 13.01.10 | 23.10 | Boiler Tube leakage |
|  |  | 29.01.10 | 06.20 | 22.03.10 | 18.35 | Annual maintenance |

4	ALLOCATION OF POWER TO DELHI

A)	Allocation from Central Sector Generating Stations to Delhi w.e.f. 15.11.2009

i) TIME BLOCK -  00.00hrs & 06.00hrs., 10.00-18hrs and 23.00-24.00hrs @ 0% from unallocated quota of Central Sector Generating Stations

All figures in MW

| Name of the Stn | Installed capacity | Total Un- allocated | Basic Allocation | Basic Allocation at periphery | Allocation out of Unallocated Quota | Allocation out of Un-allocation Quota at Delhi periphery | Total allocation at Delhi periphery |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | (8)=(5)+(7) |
| NTPC STATIONS |  |  |  |  |  |  |  |
| Singrauli STPS | 2000 | 300 | 150 | 130 | 0 | 0 | 130 |
| Rihand | 1000 | 150 | 100 | 87 | 0 | 0 | 87 |
| Rihand Stage -II | 1000 | 150 | 126 | 109 | 0 | 0 | 109 |
| ANTA GPS | 419 | 63 | 44 | 41 | 0 | 0 | 41 |
| Auriya GPS | 663.36 | 99 | 72 | 67 | 0 | 0 | 67 |
| Dadri GPS | 829.78 | 129 | 91 | 85 | 0 | 0 | 85 |
| Dadri NCTPS (Th) | 840 | 0 | 756 | 657 | 0 | 0 | 657 |
| Unchahaar-I TPS | 420 | 20 | 24 | 21 | 0 | 0 | 21 |
| Unchahaar-II TPS | 420 | 63 | 47 | 41 | 0 | 0 | 41 |
| Unchahaar-III TPS | 210 | 31 | 29 | 25 | 0 | 0 | 25 |
| TOTAL | 7802 | 1005 | 1439 | 1263 | 0 | 0 | 1263 |
| NHPC |  |  |  |  |  |  |  |
| Baira Suil HPS | 180 | 0 | 20 | 19 | 0 | 0 | 19 |
| Salal HPS | 690 | 0 | 80 | 76 | 0 | 0 | 76 |
| Tanakpur HEP | 94 | 0 | 12 | 11 | 0 | 0 | 11 |
| Chamera HEP | 540 | 0 | 43 | 41 | 0 | 0 | 41 |
| Chamera-II HEP | 300 | 54 | 40 | 38 | 0 | 0 | 38 |
| URI HEP | 480 | 0 | 53 | 50 | 0 | 0 | 50 |
| Dhauli Ganga HEP | 280 | 42 | 37 | 35 | 0 | 0 | 35 |
| Dulhasti HEP | 390 | 58 | 50 | 48 | 0 | 0 | 48 |
| TOTAL | 2954 | 154 | 335 | 318 | 0 | 0 | 318 |
| NPC |  |  |  |  |  |  |  |
| Narora APS | 440 | 64 | 47 | 41 | 0 | 0 | 41 |
| RAPP(B) Unit-3 APS | 220 | 33 | 0 | 0 | 0 | 0 | 0 |
| RAPP(B) Unit-4 APS | 220 | 33 | 0 | 0 | 0 | 0 | 0 |
| TOTAL | 880 | 130 | 47 | 41 | 0 | 0 | 41 |
| SVJNL |  |  |  |  |  |  |  |
| Nathpa Jhakri HEP | 1500 | 149 | 142 | 123 | 0 | 0 | 123 |
| THDC |  |  |  |  |  |  |  |
| Tehri Hydro | 1000 | 99 | 103 | 89 | 0 | 0 | 89 |
| Total | 14136 | 1537 | 2066 | 1835 | 0 | 0 | 1835 |
| Allocation from ER and Tala HEP |  |  |  |  |  |  |  |
| Farakka | 1600 | 0 | 30 | 25 | 0 | 0 | 25 |
| Kahalgaon | 840 | 0 | 63 | 53 | 0 | 0 | 53 |
| Talchar | 1000 | 0 | 0 | 0 | 0 | 0 | 0 |
| Tala HEP | 1020 | 153 | 30 | 25 | 0 | 0 | 25 |
| Mejia TPS Unit-6 | 250 | 0 | 29 | 25 | 0 | 0 | 25 |
| Kahalgaon-II | 1000 | 0 | 108 | 90 | 0 | 0 | 90 |
| Total ER | 5710 | 153 | 260 | 217 | 0 | 0 | 217 |
| Grand Total | 19846 | 1690 | 2326 | 2052 | 0 | 0 | 2052 |

ii) Time Block 06.00hrs. to 10.00hrs. @ 4% allocation from Central Sector Generating Stations (without RAPP Unit-3 & 4)

All figures in MW

| Name of the Stn | Installed capacity | Total Un- allocated | Basic Allocation | Basic Allocation at periphery | Allocation out of Unallocated Quota | Allocation out of Un-allocation Quota at Delhi periphery | Total allocation at Delhi periphery |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | (8)=(5)+(7) |
| NTPC STATIONS |  |  |  |  |  |  |  |
| Singrauli STPS | 2000 | 300 | 150 | 130 | 12 | 10 | 141 |
| Rihand | 1000 | 150 | 100 | 87 | 6 | 5 | 92 |
| Rihand Stage -II | 1000 | 150 | 126 | 109 | 6 | 5 | 115 |
| ANTA GPS | 419 | 63 | 44 | 41 | 3 | 2 | 43 |
| Auriya GPS | 663.36 | 99 | 72 | 67 | 3 | 3 | 70 |
| Dadri GPS | 829.78 | 129 | 91 | 85 | 2 | 2 | 87 |
| Dadri NCTPS (Th) | 840 | 0 | 756 | 657 | 0 | 0 | 657 |
| Unchahaar-I TPS | 420 | 20 | 24 | 21 | 1 | 1 | 22 |
| Unchahaar-II TPS | 420 | 63 | 47 | 41 | 3 | 2 | 43 |
| Unchahaar-III TPS | 210 | 31 | 29 | 25 | 1 | 1 | 26 |
| TOTAL | 7802 | 1005 | 1439 | 1263 | 36 | 32 | 1295 |
| NHPC |  |  |  |  |  |  |  |
| Baira Suil HPS | 180 | 0 | 20 | 19 | 0 | 0 | 19 |
| Salal HPS | 690 | 0 | 80 | 76 | 0 | 0 | 76 |
| Tanakpur HEP | 94 | 0 | 12 | 11 | 0 | 0 | 11 |
| Chamera HEP | 540 | 0 | 43 | 41 | 0 | 0 | 41 |
| Chamera-II HEP | 300 | 54 | 40 | 38 | 2 | 2 | 40 |
| URI HEP | 480 | 0 | 53 | 50 | 0 | 0 | 50 |
| Dhauli Ganga HEP | 280 | 42 | 37 | 35 | 2 | 2 | 37 |
| Dulhasti HEP | 390 | 58 | 50 | 48 | 2 | 2 | 50 |
| TOTAL | 2954 | 154 | 335 | 318 | 6 | 6 | 324 |
| NPC |  |  |  |  |  |  |  |
| Narora APS | 440 | 64 | 47 | 41 | 3 | 2 | 43 |
| RAPP(B) Unit-3 APS | 220 | 33 | 0 | 0 | 0 | 0 | 0 |
| RAPP(B) Unit-4 APS | 220 | 33 | 0 | 0 | 0 | 0 | 0 |
| TOTAL | 880 | 130 | 47 | 41 | 3 | 2 | 43 |
| SVJNL |  |  |  |  |  |  |  |
| Nathpa Jhakri HEP | 1500 | 149 | 142 | 123 | 6 | 6 | 129 |
| THDC |  |  |  |  |  |  |  |
| Tehri Hydro | 1000 | 99 | 103 | 89 | 4 | 4 | 93 |
| Total | 14136 | 1537 | 2066 | 1835 | 55 | 50 | 1884 |
| Allocation from ER and Tala HEP |  |  |  |  |  |  |  |
| Farakka | 1600 | 0 | 30 | 25 | 0 | 0 | 25 |
| Kahalgaon | 840 | 0 | 63 | 53 | 0 | 0 | 53 |
| Talchar | 1000 | 0 | 0 | 0 | 0 | 0 | 0 |
| Tala HEP | 1020 | 153 | 30 | 25 | 0 | 0 | 25 |
| Mejia TPS Unit-6 | 250 | 0 | 29 | 25 | 0 | 0 | 25 |
| Kahalgaon-II | 1000 | 0 | 108 | 90 | 2 | 2 | 92 |
| Total ER | 5710 | 153 | 260 | 217 | 2 | 2 | 219 |
| Grand Total | 19846 | 1690 | 2326 | 2052 | 57 | 51 | 2103 |

iii) Time Block 18.00hrs. to 23.00hrs. @ 4% allocation from Central Sector Generating Stations including RAPP Unit-3 & 4

All figures in MW

| Name of the Stn | Installed capacity | Total Un- allocated | Basic Allocation | Basic Allocation at periphery | Allocation out of Unallocated Quota | Allocation out of Un-allocation Quota at Delhi periphery | Total allocation at Delhi periphery |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | (8)=(5)+(7) |
| NTPC STATIONS |  |  |  |  |  |  |  |
| Singrauli STPS | 2000 | 300 | 150 | 130 | 12 | 10 | 141 |
| Rihand | 1000 | 150 | 100 | 87 | 6 | 5 | 92 |
| Rihand Stage -II | 1000 | 150 | 126 | 109 | 6 | 5 | 115 |
| ANTA GPS | 419 | 63 | 44 | 41 | 3 | 2 | 43 |
| Auriya GPS | 663.36 | 99 | 72 | 67 | 3 | 3 | 70 |
| Dadri GPS | 829.78 | 129 | 91 | 85 | 2 | 2 | 87 |
| Dadri NCTPS (Th) | 840 | 0 | 756 | 657 | 0 | 0 | 657 |
| Unchahaar-I TPS | 420 | 20 | 24 | 21 | 1 | 1 | 22 |
| Unchahaar-II TPS | 420 | 63 | 47 | 41 | 3 | 2 | 43 |
| Unchahaar-III TPS | 210 | 31 | 29 | 25 | 1 | 1 | 26 |
| TOTAL | 7802 | 1005 | 1439 | 1263 | 36 | 32 | 1295 |
| NHPC |  |  |  |  |  |  |  |
| Baira Suil HPS | 180 | 0 | 20 | 19 | 0 | 0 | 19 |
| Salal HPS | 690 | 0 | 80 | 76 | 0 | 0 | 76 |
| Tanakpur HEP | 94 | 0 | 12 | 11 | 0 | 0 | 11 |
| Chamera HEP | 540 | 0 | 43 | 41 | 0 | 0 | 41 |
| Chamera-II HEP | 300 | 54 | 40 | 38 | 2 | 2 | 40 |
| URI HEP | 480 | 0 | 53 | 50 | 0 | 0 | 50 |
| Dhauli Ganga HEP | 280 | 42 | 37 | 35 | 2 | 2 | 37 |
| Dulhasti HEP | 390 | 58 | 50 | 48 | 2 | 2 | 50 |
| TOTAL | 2954 | 154 | 335 | 318 | 6 | 6 | 324 |
| NPC |  |  |  |  |  |  |  |
| Narora APS | 440 | 64 | 47 | 41 | 3 | 2 | 43 |
| RAPP(B) Unit-3 APS | 220 | 33 | 0 | 0 | 1 | 1 | 1 |
| RAPP(B) Unit-4 APS | 220 | 33 | 0 | 0 | 1 | 1 | 1 |
| TOTAL | 880 | 130 | 47 | 41 | 4 | 3 | 44 |
| SVJNL |  |  |  |  |  |  |  |
| Nathpa Jhakri HEP | 1500 | 149 | 142 | 123 | 6 | 6 | 129 |
| THDC |  |  |  |  |  |  |  |
| Tehri Hydro | 1000 | 99 | 103 | 89 | 4 | 4 | 93 |
| Total | 14136 | 1537 | 2066 | 1835 | 56 | 51 | 1886 |
| Allocation from ER and Tala HEP |  |  |  |  |  |  |  |
| Farakka | 1600 | 0 | 30 | 25 | 0 | 0 | 25 |
| Kahalgaon | 840 | 0 | 63 | 53 | 0 | 0 | 53 |
| Talchar | 1000 | 0 | 0 | 0 | 0 | 0 | 0 |
| Tala HEP | 1020 | 153 | 30 | 25 | 0 | 0 | 25 |
| Mejia TPS Unit-6 | 250 | 0 | 29 | 25 | 0 | 0 | 25 |
| Kahalgaon-II | 1000 | 0 | 108 | 90 | 2 | 2 | 92 |
| Total ER | 5710 | 153 | 260 | 217 | 2 | 2 | 219 |
| Grand Total | 19846 | 1690 | 2326 | 2052 | 59 | 53 | 2104 |

5	ALLOCATION OF POWER TO VARIOUS LISCENCEES AS PER ORDER OF DERC AND DECISION OF GNCTD FOR ALLOCATION OF CENTRAL SECTOR STATIONS (EXCEPT DADRI THERMAL AND BTPS) AND STATE SECTOR GENERATING STATIONS w.e.f. 01.07.2009.

(Allocation In % )

i)	Allocation during the period 00.00 - 10.00hrs. and 17.00 - 24.00hrs.

| SOURCES | LICENSEES |
| --- | --- |
|  | NDMC | MES | NDPL | BRPL | BYPL | TOTAL |
| 1. Central Sector without Dadri (Th) | 00.00 | 00.00 | 29.18 | 43.58 | 27.24 | 100.00 |
| 2. Dadri (Th) | 14.05 | 00.00 | 23.89 | 36.36 | 27.70 | 100.00 |
| 3. BTPS | 15.07 | 7.09 | 21.61 | 32.90 | 23.33 | 100.00 |
| 4. IP | 00.00 | 00.00 | 28.02 | 42.51 | 29.47 | 100.00 |
| 5. RPH | 00.00 | 00.00 | 27.99 | 42.48 | 29.53 | 100.00 |
| 6. GT | 00.00 | 00.00 | 27.99 | 42.48 | 29.53 | 100.00 |
| 7. Pragati | 25.76 | 00.00 | 20.47 | 31.26 | 22.51 | 100.00 |

ii)	Allocation during the period 10.00 - 17.00hrs.

| SOURCES | LICENSEES |
| --- | --- |
|  | NDMC | MES | NDPL | BRPL | BYPL | TOTAL |
| 1. Central Sector without Dadri (Th) | 00.00 | 00.00 | 29.18 | 43.58 | 27.24 | 100.00 |
| 2. Dadri (Th) | 14.91 | 00.00 | 23.89 | 35.50 | 25.70 | 100.00 |
| 3. BTPS | 15.87 | 7.09 | 21.61 | 32.10 | 23.33 | 100.00 |
| 4. IP | 00.83 | 00.00 | 28.02 | 41.68 | 29.47 | 100.00 |
| 5. RPH | 00.86 | 00.00 | 27.99 | 41.62 | 29.53 | 100.00 |
| 6. GT | 00.86 | 00.00 | 27.99 | 41.62 | 29.53 | 100.00 |
| 7. Pragati | 26.61 | 00.00 | 20.47 | 30.41 | 22.51 | 100.00 |

6	POWER AVAILABILITY-DEMAND POSITION AT THE TIME OF PEAK DEMAND MET DURING FEBRUARY 2010

All figures in MW

| Date | Time of peak demand | Generation within Delhi | Import from the Grid | Schedule from the Grid | OD(-) / UD(+) | Demand met | Shedding | Un-Restricted Demand |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | IP | RPH | GT | PPCL | BTPS | Total |  |  |  |  |  |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8)= (3) to (7) | (9) | (10) | (11)= (10) -(9) | (12)= (10)+ (11) | (13) | (14)= (12)+ (13) |
| 1 | 08:18:18 | 0 | 44 | 171 | 299 | 430 | 944 | 1936 | 2458 | 522 | 2880 | 32 | 2912 |
| 2 | 08:28:10 | 0 | 45 | 169 | 300 | 430 | 944 | 2036 | 2197 | 161 | 2980 | 30 | 3010 |
| 3 | 07:57:19 | 0 | 43 | 179 | 300 | 441 | 963 | 2113 | 1993 | -120 | 3076 | 13 | 3089 |
| 4 | 08:12:00 | 0 | 45 | 151 | 304 | 362 | 862 | 2172 | 2144 | -28 | 3034 | 25 | 3059 |
| 5 | 09:46:24 | 0 | 47 | 111 | 294 | 427 | 879 | 2223 | 2132 | -91 | 3102 | 0 | 3102 |
| 6 | 08:27:47 | 0 | 46 | 179 | 194 | 441 | 860 | 2069 | 2245 | 176 | 2929 | 27 | 2956 |
| 7 | 09:56:52 | 0 | 44 | 160 | 281 | 449 | 934 | 1917 | 2087 | 170 | 2851 | 0 | 2851 |
| 8 | 09:43:19 | 0 | 45 | 180 | 284 | 444 | 953 | 1865 | 2268 | 403 | 2818 | 0 | 2818 |
| 9 | 19:02:28 | 0 | 46 | 149 | 296 | 433 | 924 | 1868 | 2168 | 300 | 2792 | 40 | 2832 |
| 10 | 10:17:01 | 0 | 46 | 186 | 269 | 400 | 901 | 2070 | 2141 | 71 | 2971 | 3 | 2974 |
| 11 | 09:36:28 | 0 | 46 | 187 | 294 | 441 | 968 | 1924 | 2216 | 292 | 2892 | 0 | 2892 |
| 12 | 10:04:55 | 0 | 47 | 186 | 295 | 436 | 964 | 2232 | 2418 | 186 | 3196 | 0 | 3196 |
| 13 | 09:50:37 | 0 | 49 | 183 | 282 | 432 | 946 | 1928 | 2268 | 340 | 2874 | 0 | 2874 |
| 14 | 10:05:02 | 0 | 51 | 181 | 295 | 440 | 967 | 1913 | 1669 | -244 | 2880 | 2 | 2882 |
| 15 | 10:03:55 | 0 | 52 | 188 | 156 | 430 | 826 | 2084 | 1750 | -334 | 2910 | 0 | 2910 |
| 16 | 08:25:02 | 0 | 49 | 179 | 297 | 432 | 957 | 1952 | 2390 | 438 | 2909 | 26 | 2935 |
| 17 | 10:02:29 | 0 | 49 | 178 | 131 | 430 | 788 | 2149 | 2247 | 98 | 2937 | 0 | 2937 |
| 18 | 09:31:36 | 0 | 51 | 143 | 156 | 446 | 796 | 2135 | 1989 | -146 | 2931 | 0 | 2931 |
| 19 | 09:25:43 | 0 | 52 | 176 | 320 | 494 | 1042 | 1998 | 1999 | 1 | 3040 | 0 | 3040 |
| 20 | 09:47:55 | 0 | 0 | 161 | 319 | 445 | 925 | 1979 | 2315 | 336 | 2904 | 0 | 2904 |
| 21 | 09:20:18 | 0 | 0 | 95 | 305 | 465 | 865 | 2030 | 2082 | 52 | 2895 | 5 | 2900 |
| 22 | 08:30:00 | 0 | 0 | 150 | 300 | 434 | 884 | 1914 | 2290 | 376 | 2798 | 23 | 2821 |
| 23 | 19:00:00 | 0 | 51 | 164 | 314 | 443 | 972 | 1785 | 2216 | 431 | 2757 | 28 | 2785 |
| 24 | 09:44:24 | 0 | 50 | 169 | 295 | 233 | 747 | 2083 | 2158 | 75 | 2830 | 0 | 2830 |
| 25 | 19:04:39 | 0 | 52 | 125 | 264 | 240 | 681 | 2150 | 2146 | -4 | 2831 | 13 | 2844 |
| 26 | 09:52:31 | 0 | 52 | 144 | 288 | 378 | 862 | 2015 | 2049 | 34 | 2877 | 0 | 2877 |
| 27 | 09:51:01 | 0 | 50 | 144 | 313 | 361 | 868 | 1862 | 2068 | 206 | 2730 | 0 | 2730 |
| 28 | 10:01:12 | 0 | 51 | 144 | 316 | 430 | 941 | 1600 | 2156 | 556 | 2541 | 0 | 2541 |

7	POWER AVAILABILITY- DEMAND POSITION AT THE TIME OF MAXIMUM UNRESTRICTED DEMAND DURING FEBRUARY 2010

All figures in MW

| Date | Time of peak demand | Generation within Delhi | Import from the Grid | Schedule from the Grid | OD(-) / UD(+) | Demand met | Shedding | Un-Restricted Demand |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | IP | RPH | GT | PPCL | BTPS | Total |  |  |  |  |  |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8)=(3) to (7) | (9) | (10) | (11)= (10) -(9) | (12)=(10) + (11) | (13) | (14)= (12)+ (13) |
| 1 | 08:18:18 | 0 | 44 | 171 | 299 | 430 | 944 | 1936 | 2458 | 522 | 2880 | 32 | 2912 |
| 2 | 08:28:10 | 0 | 45 | 169 | 300 | 430 | 944 | 2036 | 2197 | 161 | 2980 | 30 | 3010 |
| 3 | 07:57:19 | 0 | 43 | 179 | 300 | 441 | 963 | 2113 | 1993 | -120 | 3076 | 13 | 3089 |
| 4 | 08:12:00 | 0 | 45 | 151 | 304 | 362 | 862 | 2172 | 2144 | -28 | 3034 | 25 | 3059 |
| 5 | 09:46:24 | 0 | 47 | 111 | 294 | 427 | 879 | 2223 | 2132 | -91 | 3102 | 0 | 3102 |
| 6 | 08:27:47 | 0 | 46 | 179 | 194 | 441 | 860 | 2069 | 2245 | 176 | 2929 | 27 | 2956 |
| 7 | 09:56:52 | 0 | 44 | 160 | 281 | 449 | 934 | 1917 | 2087 | 170 | 2851 | 0 | 2851 |
| 8 | 09:43:19 | 0 | 45 | 180 | 284 | 444 | 953 | 1865 | 2268 | 403 | 2818 | 0 | 2818 |
| 9 | 19:02:28 | 0 | 46 | 149 | 296 | 433 | 924 | 1868 | 2168 | 300 | 2792 | 40 | 2832 |
| 10 | 10:17:01 | 0 | 46 | 186 | 269 | 400 | 901 | 2070 | 2141 | 71 | 2971 | 3 | 2974 |
| 11 | 09:36:28 | 0 | 46 | 187 | 294 | 441 | 968 | 1924 | 2216 | 292 | 2892 | 0 | 2892 |
| 12 | 10:04:55 | 0 | 47 | 186 | 295 | 436 | 964 | 2232 | 2418 | 186 | 3196 | 0 | 3196 |
| 13 | 09:50:37 | 0 | 49 | 183 | 282 | 432 | 946 | 1928 | 2268 | 340 | 2874 | 0 | 2874 |
| 14 | 10:05:02 | 0 | 51 | 181 | 295 | 440 | 967 | 1913 | 1669 | -244 | 2880 | 2 | 2882 |
| 15 | 10:03:55 | 0 | 52 | 188 | 156 | 430 | 826 | 2084 | 1750 | -334 | 2910 | 0 | 2910 |
| 16 | 08:25:02 | 0 | 49 | 179 | 297 | 432 | 957 | 1952 | 2390 | 438 | 2909 | 26 | 2935 |
| 17 | 10:02:29 | 0 | 49 | 178 | 131 | 430 | 788 | 2149 | 2247 | 98 | 2937 | 0 | 2937 |
| 18 | 09:31:36 | 0 | 51 | 143 | 156 | 446 | 796 | 2135 | 1989 | -146 | 2931 | 0 | 2931 |
| 19 | 09:25:43 | 0 | 52 | 176 | 320 | 494 | 1042 | 1998 | 1999 | 1 | 3040 | 0 | 3040 |
| 20 | 09:47:55 | 0 | 0 | 161 | 319 | 445 | 925 | 1979 | 2315 | 336 | 2904 | 0 | 2904 |
| 21 | 09:20:18 | 0 | 0 | 95 | 305 | 465 | 865 | 2030 | 2082 | 52 | 2895 | 5 | 2900 |
| 22 | 08:30:00 | 0 | 0 | 150 | 300 | 434 | 884 | 1914 | 2290 | 376 | 2798 | 23 | 2821 |
| 23 | 19:00:00 | 0 | 51 | 164 | 314 | 443 | 972 | 1785 | 2216 | 431 | 2757 | 28 | 2785 |
| 24 | 09:44:24 | 0 | 50 | 169 | 295 | 233 | 747 | 2083 | 2158 | 75 | 2830 | 0 | 2830 |
| 25 | 19:04:39 | 0 | 52 | 125 | 264 | 240 | 681 | 2150 | 2146 | -4 | 2831 | 13 | 2844 |
| 26 | 09:52:31 | 0 | 52 | 144 | 288 | 378 | 862 | 2015 | 2049 | 34 | 2877 | 0 | 2877 |
| 27 | 09:51:01 | 0 | 50 | 144 | 313 | 361 | 868 | 1862 | 2068 | 206 | 2730 | 0 | 2730 |
| 28 | 10:01:12 | 0 | 51 | 144 | 316 | 430 | 941 | 1600 | 2156 | 556 | 2541 | 0 | 2541 |

8 	SOURCEWISE SCHEDULED DRAWL FROM NORTHERN GRID AS WELL AS

AVAILABILITY WITHIN DELHI FOR FEBUARY 2010

A)   AVAILABILITY FROM GENCO AND PRAGATI STNs. (all fig in MUs)

| (I) IP | 0.000 |
| --- | --- |
| (II)NET IP GENERATION | 0.000 |
| (III) RPH | 30.395 |
| JHAJJAR SHARE | 0.616 |
| IV) NET RPH | 29.779 |
| (V) GT+WHRU | 111.519 |
| (VI) PRAGATI | 188.786 |
| TOTAL | 330.084 |
| B) AVAILABILITY FROM BTPS | 280.404 |
| C) AUXILIARY CONSUMPTION OF GENERATING STNs. EXCLUDING BTPS | 13.632 |
| D) NET GENERATION AVAILABLE WITHIN DELHI (A+B-C) | 596.856 |

B)  SOURCE WISE SCHEDULED DRAWL FROM THE NORTHERN GRID

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT DELHI PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT DELHI PERIPHERY |
| --- | --- | --- | --- | --- |
| B/SUIL | 3.911 | 3.736 | 3.911 | 3.736 |
| SALAL | 11.824 | 11.291 | 11.824 | 11.291 |
| TANAKPUR | 1.948 | 1.860 | 1.948 | 1.860 |
| CHAMERA | 5.039 | 4.814 | 5.039 | 4.814 |
| CHAMERA-II | 5.324 | 5.085 | 5.324 | 5.085 |
| DHAULI GANGA | 3.686 | 3.519 | 3.686 | 3.519 |
| SINGRAULI | 98.073 | 93.598 | 97.254 | 92.816 |
| URI | 20.815 | 19.883 | 20.815 | 19.883 |
| ANTA (GAS) | 14.560 | 13.897 | 14.412 | 13.756 |
| ANTA (LIQUID) | 2.089 | 1.994 | 0.024 | 0.023 |
| ANTA (RLNG) | 12.830 | 12.242 | 1.375 | 1.311 |
| RIHAND-I | 66.220 | 63.198 | 65.703 | 62.704 |
| RIHAND-II | 84.103 | 80.266 | 83.438 | 79.630 |
| AURAIYA (GAS) | 32.888 | 31.390 | 32.637 | 31.150 |
| AURAIYA (LIQUID) | 8.304 | 7.918 | 0.212 | 0.202 |
| AURAIYA (RLNG) | 6.186 | 5.910 | 0.583 | 0.556 |
| DADRI(GT) (GAS) | 36.270 | 34.618 | 35.879 | 34.246 |
| DADRI(GT) (LIQUID) | 8.777 | 8.368 | 0.224 | 0.213 |
| DADRI(GT) (RLNG) | 15.435 | 14.740 | 1.464 | 1.396 |
| UNCHAHAR-I | 15.652 | 14.937 | 13.723 | 13.098 |
| UNCHAHAR-III | 18.724 | 17.870 | 16.537 | 15.783 |
| DADRI(TH) | 486.009 | 463.832 | 463.059 | 441.933 |
| UNCHAHAR-II | 30.563 | 29.168 | 26.869 | 25.645 |
| NAPP | 7.863 | 7.504 | 7.863 | 7.504 |
| RAPP-B | 1.219 | 1.163 | 1.197 | 1.142 |
| RAPP-C | 13.274 | 12.679 | 11.444 | 10.931 |
| GUJARAT | 55.682 | 52.485 | 52.517 | 50.081 |
| GUJARAT | 50.060 | 47.192 | 45.217 | 43.121 |
| TO MEGHALAYA | -2.879 | -2.961 | -2.961 | -3.103 |
| TO ORISSA | -1.792 | -1.844 | -1.844 | -1.921 |
| DVC (ER) | 28.800 | 28.003 | 28.003 | 26.717 |
| MAHARASHTRA | 14.865 | 13.998 | 13.319 | 12.720 |

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT DELHI PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT DELHI PERIPHERY |
| --- | --- | --- | --- | --- |
| CHHATTISGARH (WR) | 68.897 | 64.927 | 61.683 | 58.874 |
| ANDHRA PRADESH | 8.051 | 7.634 | 7.424 | 7.087 |
| TO TAMILNADU | -15.359 | -15.793 | -15.793 | -16.548 |
| PUNJAB | 21.790 | 19.413 | 19.413 | 18.518 |
| TO MADHYA PRADESH | -19.846 | -21.057 | -21.057 | -22.064 |
| TO UTTAR PRADESH | -18.370 | -19.306 | -4.585 | -4.827 |
| HARYANA | 11.217 | 10.706 | 11.217 | 10.706 |
| TO HIMACHAL PRADESH | -54.036 | -56.625 | -54.036 | -56.625 |
| TO UTTRANCHAL | -42.115 | -44.128 | -42.115 | -44.128 |
| TO KARNATAKA | -31.122 | -32.008 | -32.008 | -33.381 |
| KARNATAKA | 55.157 | 52.312 | 48.839 | 46.608 |
| TO POWER EXCHANGE (IEX) | -194.758 | -203.929 | -194.758 | -203.929 |
| POWER EXCHANGE (IEX) | 1.020 | 0.970 | 1.020 | 0.970 |
| TO POWER EXCHANGE (PX) | -2.028 | -2.126 | -2.028 | -2.126 |
| POWER EXCHANGE (PX) | 0.000 | 0.000 | 0.000 | 0.000 |
| NATHPA JHAKARI | 18.109 | 17.285 | 18.109 | 17.285 |
| DULHASTI | 9.985 | 9.531 | 9.985 | 9.531 |
| TEHRI | 24.385 | 23.272 | 24.385 | 23.272 |
| KEHALGAON-II | 58.189 | 56.586 | 53.387 | 50.962 |
| TALA | 0.541 | 0.526 | 0.526 | 0.501 |
| FARAKKA | 17.057 | 16.587 | 15.622 | 14.909 |
| KAHALGAON0I | 37.332 | 36.308 | 34.606 | 33.032 |
| DADRI (TH)-II | 204.221 | 195.056 | 197.766 | 188.887 |
| TOTAL SCHEDULE FROM THE GRID | 1314.638 | 1218.493 | 1198.294 | 1109.356 |

C)   AGENCY WISE BREAKUP OF ENERGY SCHEDULED DRAWL FROM THE GRID

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT POWER PERIPHERY |
| --- | --- | --- | --- | --- |
| NTPC – NR | 936.681 | 893.946 | 853.391 | 814.462 |
| NTPC –ER | 112.579 | 109.481 | 103.615 | 98.904 |
| NHPC | 62.533 | 59.720 | 62.533 | 59.720 |
| NPC | 22.355 | 21.346 | 20.503 | 19.577 |
| GUJARAT | 50.062 | 47.192 | 45.217 | 43.121 |
| GUJARAT | 55.682 | 52.485 | 52.517 | 50.081 |
| CHHATTISGARH (WR) | 68.897 | 64.927 | 61.683 | 58.874 |
| ANDHRA PRADESH | 8.051 | 7.634 | 7.424 | 7.087 |
| PUNJAB | 21.790 | 19.413 | 19.413 | 18.518 |
| DVC (ER) | 28.800 | 28.003 | 28.003 | 26.717 |
| KARNATAKA | 55.157 | 52.312 | 48.839 | 46.608 |
| HARYANA | 11.217 | 10.706 | 11.217 | 10.706 |
| MAHARASHTRA | 14.865 | 13.998 | 13.319 | 12.720 |
| POWER EXCHANGE (IEX) | 1.020 | 0.970 | 1.020 | 0.970 |
| NATHPA JHAKARI | 18.109 | 17.285 | 18.109 | 17.285 |
| TEHRI | 24.385 | 23.272 | 24.385 | 23.272 |
| TALA | 0.541 | 0.526 | 0.526 | 0.501 |
| DADRI (TH)-II | 204.221 | 195.056 | 197.766 | 188.887 |
| POWER EXCHANGE-PX | 0.000 | 0.000 | 0.000 | 0.000 |
| TOTAL SCHEDULE FROM THE GRID | 1696.944 | 1618.270 | 1569.480 | 1498.012 |

D) AGENCY WISE BREAKUP OF ENERGY SCHEDULED BY NRLDC FOR EXPORT TO OTHER UTILITIES FROM DTL

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT POWER PERIPHERY |
| --- | --- | --- | --- | --- |
| TO ORISSA | -1.792 | -1.844 | -1.844 | -1.921 |
| TO UTTAR PRADESH | -18.370 | -19.306 | -4.585 | -4.827 |
| TO HIMACHAL PRADESH | -54.036 | -56.625 | -54.036 | -56.625 |
| TO MEGHALAYA | -2.879 | -2.961 | -2.961 | -3.103 |
| TO KARNATAKA | -31.122 | -32.008 | -32.008 | -33.381 |
| TO TAMIL NADU | -15.359 | -15.793 | -15.793 | -16.548 |
| TO POWER EXCHANGE - PX | -2.028 | -2.126 | -2.028 | -2.126 |
| TO MADHYA PRADESH | -19.846 | -21.057 | -21.057 | -22.064 |
| TO UTTRANCHAL | -42.115 | -44.128 | -42.115 | -44.128 |
| TO J&K | 0.000 | 0.000 | 0.000 | 0.000 |
| TO POWER EXCHANGE - IEX | -194.758 | -203.929 | -194.758 | -203.929 |
| TOTAL | -382.306 | -399.777 | -371.186 | -388.652 |
| (G) TOTAL SCHEDULED DRAWL FROM THE GRID (G=Fa+Fb+Fc) | 1314.638 | 1218.493 | 1198.294 | 1109.360 |
| TOTAL CONSUMPTION INCLUDING AUX. OF GENERATING STNs. EXCLUDING BTPS | 1425.449 |
| NET CONSUMPTION | 1411.817 |
| AVAILABILITY WITHIN DELHI | 596.856 |
| ACTUAL DRAWAL FROM THE GRID | 814.961 |
| OVER DRAWAL(+)/UNDER DRAWAL(-) FROM THE GRID ON THE BASIS OF SCHEDULED ALLOCATION MADE BY NRLDC TO DELHI AT PERIPHERY | (-)294.399 |
| LOAD SHEDDING | 5.223 |
| UNRESTRICTED DEMAND (GROSS) | 1430.672 |
| UNRESTRICTED DEMAND (NET) | 1417.040 |
| MAX. NET CONSUMPTION | 53.344 Mus. ON 05.02.2010 |
| MAX. LOAD SHEDDING | 419 MW ON 14.02.2010 AT 17.38HRS. |
| PEAK LOAD DAY PEAK EVENING PEAK | Peak Demand during the month 3196MW AT 10:04:55HRS ON 12.02.2010 2939MW AT 19:00.00HRS ON 02.02.2010 | SHEDDING AT PEAK TIME NIL 25MW |
| P.L.F. OF GENCO AND PRAGATI STNs. | IP RPH GT PRAGATI | 0.00% 33.50% 61.46% 85.13% |

9	SHEDDING DETAILS DURING THE MONTH OF FEBUARY 2010.

### ALL FIGURES IN MUs

| DATE | No. of Under Freq. Relay Operated | Shedding due to under frequency relay operation in MUs | Shedding due to Grid Restrictions (Over drawal / low freq.) |
| --- | --- | --- | --- |
|  |  | BSES | NDPL | NDMC | TOTAL | BSES | NDPL | NDMC |
|  |  | BYPL | BRPL |  |  |  | BYPL | BRPL |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7=3 to 6 | 8 | 9 | 10 | 11 |
| 01-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 02-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 03-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 04-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 05-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 06-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 07-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 08-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 09-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 10-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 11-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 12-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 13-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 14-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 15-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 16-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 17-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 18-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 19-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 20-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 21-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 22-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 23-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 24-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 25-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 26-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 27-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 28-Feb-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| TOTAL | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |

#### ALL FIGURES IN MUs

| Date | Shedding due to Transmission/Grid Constraints in Central Sector Stations / TTC / ATC VOILATION | TOTAL | TOTAL SHEDDING DUE TO GRID RESTRIC TIONS | Due to T&D Constraints |
| --- | --- | --- | --- | --- |
|  |  |  |  | DTL |
|  | BSES | NDPL | NDMC |  |  | BSES | NDPL | NDMC | MES |
|  | BYPL | BRPL |  |  |  |  | BYPL | BRPL |  |  |  |
| 1 | 12 | 13 | 14 | 15 | 16=8to15 | 17=16+7 | 18 | 19 | 20 | 21 | 22 |
| 01-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.009 | 0.000 | 0.000 | 0.000 | 0.000 |
| 02-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 03-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 04-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.008 | 0.000 | 0.000 | 0.000 | 0.000 |
| 05-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.071 | 0.000 | 0.000 | 0.000 | 0.000 |
| 06-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.076 | 0.004 | 0.000 | 0.000 | 0.000 |
| 07-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 08-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.013 | 0.000 | 0.057 | 0.000 | 0.000 |
| 09-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.003 | 0.000 | 0.000 | 0.000 | 0.000 |
| 10-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 11-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 12-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 13-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 14-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.305 | 0.004 | 0.026 | 0.003 | 0.000 |
| 15-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.011 | 0.000 | 0.000 |
| 16-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 17-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 18-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.003 | 0.000 | 0.000 |
| 19-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 20-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 21-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 22-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 23-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.015 | 0.002 | 0.001 | 0.002 | 0.000 |
| 24-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.001 | 0.000 |
| 25-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 26-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 27-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 28-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| TOTAL | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.500 | 0.010 | 0.098 | 0.006 | 0.000 |

| DATE | DUE TO T&D CONTRAINTS | OTHER AGENCIES LIKE GENCO, BBMB, BTPS ETC. | THEFT PRONE SHEDDING | TOTAL SHEDDING DUE TO T&D CONSTS. & THEFT PRONE | GRAND TOTAL |
| --- | --- | --- | --- | --- | --- |
|  | DISCOMS |  |  |  |  |
|  | BSES | NDPL |  | BSES | NDPL |  |  |
|  | BYPL | BRPL |  |  | BYPL | BRPL |  |  |  |
| 1 | 23 | 24 | 25 | 2+ | 27 | 28 | 29 | 30=18 to29 | 31=30+17 |
| 01-Feb-10 | 0.015 | 0.015 | 0.001 | 0.000 | 0.000 | 0.000 | 0.156 | 0.196 | 0.196 |
| 02-Feb-10 | 0.000 | 0.011 | 0.000 | 0.000 | 0.000 | 0.000 | 0.157 | 0.168 | 0.168 |
| 03-Feb-10 | 0.000 | 0.018 | 0.001 | 0.000 | 0.000 | 0.000 | 0.152 | 0.171 | 0.171 |
| 04-Feb-10 | 0.012 | 0.028 | 0.000 | 0.000 | 0.000 | 0.000 | 0.158 | 0.206 | 0.206 |
| 05-Feb-10 | 0.005 | 0.016 | 0.000 | 0.000 | 0.000 | 0.000 | 0.140 | 0.232 | 0.232 |
| 06-Feb-10 | 0.017 | 0.013 | 0.001 | 0.000 | 0.000 | 0.000 | 0.161 | 0.272 | 0.272 |
| 07-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.141 | 0.141 | 0.141 |
| 08-Feb-10 | 0.000 | 0.016 | 0.024 | 0.000 | 0.000 | 0.000 | 0.108 | 0.218 | 0.218 |
| 09-Feb-10 | 0.010 | 0.022 | 0.035 | 0.000 | 0.000 | 0.000 | 0.097 | 0.167 | 0.167 |
| 10-Feb-10 | 0.000 | 0.043 | 0.002 | 0.000 | 0.000 | 0.000 | 0.153 | 0.198 | 0.198 |
| 11-Feb-10 | 0.000 | 0.052 | 0.007 | 0.000 | 0.000 | 0.000 | 0.133 | 0.192 | 0.192 |
| 12-Feb-10 | 0.000 | 0.006 | 0.067 | 0.000 | 0.000 | 0.000 | 0.136 | 0.209 | 0.209 |
| 13-Feb-10 | 0.006 | 0.016 | 0.002 | 0.000 | 0.000 | 0.000 | 0.141 | 0.165 | 0.165 |
| 14-Feb-10 | 0.004 | 0.005 | 0.000 | 0.000 | 0.000 | 0.000 | 0.104 | 0.451 | 0.451 |
| 15-Feb-10 | 0.040 | 0.000 | 0.016 | 0.000 | 0.000 | 0.000 | 0.133 | 0.200 | 0.200 |
| 16-Feb-10 | 0.012 | 0.033 | 0.000 | 0.000 | 0.000 | 0.000 | 0.121 | 0.166 | 0.166 |
| 17-Feb-10 | 0.000 | 0.042 | 0.036 | 0.000 | 0.000 | 0.000 | 0.132 | 0.210 | 0.210 |
| 18-Feb-10 | 0.013 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.147 | 0.163 | 0.163 |
| 19-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.128 | 0.128 | 0.128 |
| 20-Feb-10 | 0.000 | 0.000 | 0.001 | 0.000 | 0.000 | 0.000 | 0.154 | 0.155 | 0.155 |
| 21-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.134 | 0.134 | 0.134 |
| 22-Feb-10 | 0.000 | 0.007 | 0.000 | 0.000 | 0.000 | 0.000 | 0.129 | 0.136 | 0.136 |
| 23-Feb-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.129 | 0.149 | 0.149 |
| 24-Feb-10 | 0.018 | 0.000 | 0.037 | 0.021 | 0.000 | 0.000 | 0.124 | 0.201 | 0.201 |
| 25-Feb-10 | 0.000 | 0.016 | 0.000 | 0.000 | 0.000 | 0.000 | 0.138 | 0.154 | 0.154 |
| 26-Feb-10 | 0.003 | 0.000 | 0.001 | 0.000 | 0.000 | 0.000 | 0.147 | 0.151 | 0.151 |
| 27-Feb-10 | 0.000 | 0.018 | 0.025 | 0.000 | 0.000 | 0.000 | 0.136 | 0.179 | 0.179 |
| 28-Feb-10 | 0.001 | 0.024 | 0.000 | 0.000 | 0.000 | 0.000 | 0.086 | 0.111 | 0.111 |
| TOTAL | 0.156 | 0.401 | 0.256 | 0.021 | 0.000 | 0.000 | 3.775 | 5.223 | 5.223 |

| DATE | (NET CONS.) | MAXI. DEMAND MET DURING THE DAY | TIME OF OCCUR-RENCE OF MAX DEMAND | SHEDDING AT THIS TIME | UN-REST- RICTED DEMAND | MAXIMUM UN-REST-RICTED DEMAND DURING THE DAY | TIME OF MAX. UN-REST. DEMAND | DEMAND AT THAT TIME | SHEDDING AT THAT TIME |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | In Mus. | IN MW | IN HRS. | IN MW | IN MW | IN MW | HRS. | IN MW | IN MW |
| 1 | 32 | 33 | 34 | 35 | 36=33+35 | 37=39+40 | 38 | 39 | 40 |
| 01-Feb-10 | 51.663 | 2880 | 08:18:18 | 32 | 2912 | 2912 | 08:18:18 | 2880 | 32 |
| 02-Feb-10 | 52.306 | 2980 | 08:28:10 | 30 | 3010 | 3010 | 08:28:10 | 2980 | 30 |
| 03-Feb-10 | 52.817 | 3076 | 07:57:19 | 13 | 3089 | 3089 | 10:54:26 | 3076 | 13 |
| 04-Feb-10 | 52.414 | 3034 | 08:12 | 25 | 3059 | 3059 | 08:12 | 3034 | 25 |
| 05-Feb-10 | 53.344 | 3102 | 09:46:24 | 0 | 3102 | 3102 | 09:46:24 | 3102 | 0 |
| 06-Feb-10 | 50.227 | 2929 | 08:27:47 | 27 | 2956 | 2956 | 08:27:47 | 2929 | 27 |
| 07-Feb-10 | 50.439 | 2851 | 09:56:52 | 0 | 2851 | 2851 | 09:56:52 | 2851 | 0 |
| 08-Feb-10 | 48.360 | 2818 | 09:43:19 | 0 | 2818 | 2818 | 09:43:19 | 2818 | 0 |
| 09-Feb-10 | 49.012 | 2792 | 19:02:28 | 40 | 2832 | 2832 | 19:02:28 | 2792 | 40 |
| 10-Feb-10 | 52.090 | 2971 | 10:17:01 | 3 | 2974 | 2974 | 10:17:01 | 2971 | 3 |
| 11-Feb-10 | 51.397 | 2892 | 09:36:28 | 0 | 2892 | 2892 | 09:36:28 | 2892 | 0 |
| 12-Feb-10 | 51.395 | 3196 | 10:04:55 | 0 | 3196 | 3196 | 10:04:55 | 3196 | 0 |
| 13-Feb-10 | 49.721 | 2874 | 09:50:37 | 0 | 2874 | 2874 | 09:50:37 | 2874 | 0 |
| 14-Feb-10 | 47.737 | 2880 | 10:05:02 | 2 | 2882 | 2882 | 10:05:02 | 2880 | 2 |
| 15-Feb-10 | 49.609 | 2910 | 10:03:55 | 0 | 2910 | 2910 | 10:03:55 | 2910 | 0 |
| 16-Feb-10 | 50.799 | 2909 | 08:25:02 | 26 | 2935 | 2935 | 08:25:02 | 2909 | 26 |
| 17-Feb-10 | 51.134 | 2937 | 10:02:29 | 0 | 2937 | 2937 | 10:02:29 | 2937 | 0 |
| 18-Feb-10 | 51.092 | 2931 | 09:31:36 | 0 | 2931 | 2937 | 09:31:36 | 2937 | 0 |
| 19-Feb-10 | 52.163 | 3040 | 09:25:43 | 0 | 3040 | 3040 | 09:25:43 | 3040 | 0 |
| 20-Feb-10 | 49.242 | 2904 | 09:47:55 | 0 | 2904 | 2904 | 09:47:55 | 2904 | 0 |
| 21-Feb-10 | 47.575 | 2895 | 09:20:18 | 5 | 2900 | 2900 | 09:20:18 | 2895 | 5 |
| 22-Feb-10 | 50.464 | 2798 | 08:30 | 23 | 2821 | 2821 | 08:30 | 2798 | 23 |
| 23-Feb-10 | 50.254 | 2757 | 19:00 | 28 | 2785 | 2785 | 19:00 | 2757 | 28 |
| 24-Feb-10 | 50.781 | 2830 | 09:44:24 | 0 | 2830 | 2830 | 09:44:24 | 2830 | 0 |
| 25-Feb-10 | 50.314 | 2831 | 19:04:39 | 13 | 2844 | 2844 | 19:04:39 | 2831 | 13 |
| 26-Feb-10 | 51.109 | 2877 | 09:52:31 | 0 | 2877 | 2877 | 09:52:31 | 2877 | 0 |
| 27-Feb-10 | 48.986 | 2730 | 09:51:01 | 0 | 2730 | 2730 | 09:51:01 | 2730 | 0 |
| 28-Feb-10 | 45.373 | 2541 | 10:01:12 | 0 | 2541 | 2541 | 10:01:12 | 2541 | 0 |
| TOTAL | 1411.817 | 3196 |  |  | 3196 | 3196 |  |  |  |

10	LOAD PATTERN OF DELHI ON THE DAY OF PEAK DEMAND MET DURING FEBRUARY 2010 ON 12.02.2010 – 3196 MW at 10:04:55HRS.

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1.00 | 1396 | 0 | 1396 |
| 2.00 | 1310 | 0 | 1310 |
| 3.00 | 1272 | 0 | 1272 |
| 4.00 | 1309 | 0 | 1309 |
| 5.00 | 1479 | 0 | 1479 |
| 6.00 | 1880 | 0 | 1880 |
| 7.00 | 2479 | 36 | 2515 |
| 8.00 | 2919 | 51 | 2970 |
| 9.00 | 3103 | 20 | 3123 |
| 10.00 | 3158 | 0 | 3158 |
| 10.04.55 | 3196 | 0 | 3196 |
| 11.00 | 2970 | 2 | 2972 |
| 12.00 | 2511 | 31 | 2542 |
| 13.00 | 2266 | 17 | 2283 |
| 14.00 | 2115 | 2 | 2117 |
| 15.00 | 2207 | 2 | 2209 |
| 16.00 | 2181 | 2 | 2183 |
| 17.00 | 2272 | 0 | 2272 |
| 18.00 | 2540 | 20 | 2560 |
| 19.00 | 2653 | 17 | 2670 |
| 20.00 | 2573 | 2 | 2575 |
| 21.00 | 2368 | 2 | 2370 |
| 22.00 | 2119 | 0 | 2119 |
| 23.00 | 1834 | 0 | 1834 |
| 24.00 | 1526 | 0 | 1526 |
| ENERGY IN Mus | 51.395 | 0.209 | 51.604 |

11	LOAD PATTERN OF DELHI ON THE DAY OF MAXIMUM UN-RESTRICTED DEMAND DURING FEBRUARY 2010 – 12.02.2010 – 3196MW at 10:04:55hrs.

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1.00 | 1396 | 0 | 1396 |
| 2.00 | 1310 | 0 | 1310 |
| 3.00 | 1272 | 0 | 1272 |
| 4.00 | 1309 | 0 | 1309 |
| 5.00 | 1479 | 0 | 1479 |
| 6.00 | 1880 | 0 | 1880 |
| 7.00 | 2479 | 36 | 2515 |
| 8.00 | 2919 | 51 | 2970 |
| 9.00 | 3103 | 20 | 3123 |
| 10.00 | 3158 | 0 | 3158 |
| 10.04.55 | 3196 | 0 | 3196 |
| 11.00 | 2970 | 2 | 2972 |
| 12.00 | 2511 | 31 | 2542 |
| 13.00 | 2266 | 17 | 2283 |
| 14.00 | 2115 | 2 | 2117 |
| 15.00 | 2207 | 2 | 2209 |
| 16.00 | 2181 | 2 | 2183 |
| 17.00 | 2272 | 0 | 2272 |
| 18.00 | 2540 | 20 | 2560 |
| 19.00 | 2653 | 17 | 2670 |
| 20.00 | 2573 | 2 | 2575 |
| 21.00 | 2368 | 2 | 2370 |
| 22.00 | 2119 | 0 | 2119 |
| 23.00 | 1834 | 0 | 1834 |
| 24.00 | 1526 | 0 | 1526 |
| ENERGY IN Mus | 51.395 | 0.209 | 51.604 |

12	LOAD PATTERN OF DELHI ON THE DAY OF MAXIMUM ENERGY CONSUMED

DURING FEBRUARY 2010 – 05.02.2010 – 53.344 Mus

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1.00 | 1360 | 0 | 1360 |
| 2.00 | 1289 | 0 | 1289 |
| 3.00 | 1259 | 0 | 1259 |
| 4.00 | 1278 | 0 | 1278 |
| 5.00 | 1457 | 0 | 1457 |
| 6.00 | 2096 | 0 | 2096 |
| 7.00 | 2882 | 8 | 2890 |
| 8.00 | 3019 | 61 | 3080 |
| 9.00 | 3040 | 8 | 3048 |
| 10.00 | 3089 | 1 | 3090 |
| 11.00 | 2930 | 3 | 2933 |
| 12.00 | 2688 | 2 | 2690 |
| 13.00 | 2481 | 0 | 2481 |
| 14.00 | 2360 | 3 | 2363 |
| 15.00 | 2354 | 3 | 2357 |
| 16.00 | 2119 | 97 | 2216 |
| 17.00 | 2314 | 37 | 2351 |
| 18.00 | 2589 | 26 | 2615 |
| 19.00 | 2903 | 0 | 2903 |
| 20.00 | 2781 | 26 | 2807 |
| 21.00 | 2529 | 5 | 2534 |
| 22.00 | 2262 | 0 | 2262 |
| 23.00 | 2034 | 0 | 2034 |
| 24.00 | 1569 | 9 | 1578 |
| ENERGY IN Mus | 53.344 | 0.232 | 53.576 |

13	LOAD PATTERN OF DELHI ON THE DAY OF MAXIMUM UNRESTRICTED ENERGY DEMAND DURING FEBRUARY 2010 – 05.02.2010 – 53.576Mus

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1.00 | 1360 | 0 | 1360 |
| 2.00 | 1289 | 0 | 1289 |
| 3.00 | 1259 | 0 | 1259 |
| 4.00 | 1278 | 0 | 1278 |
| 5.00 | 1457 | 0 | 1457 |
| 6.00 | 2096 | 0 | 2096 |
| 7.00 | 2882 | 8 | 2890 |
| 8.00 | 3019 | 61 | 3080 |
| 9.00 | 3040 | 8 | 3048 |
| 10.00 | 3089 | 1 | 3090 |
| 11.00 | 2930 | 3 | 2933 |
| 12.00 | 2688 | 2 | 2690 |
| 13.00 | 2481 | 0 | 2481 |
| 14.00 | 2360 | 3 | 2363 |
| 15.00 | 2354 | 3 | 2357 |
| 16.00 | 2119 | 97 | 2216 |
| 17.00 | 2314 | 37 | 2351 |
| 18.00 | 2589 | 26 | 2615 |
| 19.00 | 2903 | 0 | 2903 |
| 20.00 | 2781 | 26 | 2807 |
| 21.00 | 2529 | 5 | 2534 |
| 22.00 | 2262 | 0 | 2262 |
| 23.00 | 2034 | 0 | 2034 |
| 24.00 | 1569 | 9 | 1578 |
| ENERGY IN Mus | 53.344 | 0.232 | 53.576 |

14	LOAD DURATION CURVE FOR FEBRUARY 2010

| Load in MW | Percentage of Time |
| --- | --- |
| Above 900 | 100 % |
| Above 1100 | 99.51 % |
| Above 1300 | 90.03 % |
| Above 1500 | 79.78 % |
| Above 1700 | 74.75 % |
| Above 1900 | 70.15 % |
| Above 2100 | 64.09 % |
| Above 2300 | 44.49 % |
| Above 2500 | 31.94 % |
| Above 2700 | 17.54 % |
| Above 2900 | 2.94 % |
| Above 3100 | 0.26 % |

15	FREQUENCY ANALYSIS FOR THE MONTH OF FEBUARY 2010

| Frequency Range in Hz. | Percentage of time |
| --- | --- |
| Above 48.00 | 100 % |
| Above 48.25 | 100 % |
| Above 48.50 | 100 % |
| Above 48.75 | 100 % |
| Above 49.00 | 100 % |
| Above 49.25 | 99.78 % |
| Above 49.50 | 95.53 % |
| Above 49.75 | 75.99 % |
| Above 50.00 | 33.57 % |
| Above 50.25 | 5.96 % |
| Above 50.50 | 0.45 % |
| Above 50.75 | 0 % |

16	Voltage Profile of 220 KV sub-sTATIONS in Delhi during FEBUARY 2010

All figures in kV

| Date | NARELA | GAZIPUR |
| --- | --- | --- |
|  | Max | Min | Max | Min |
| 01-Feb-10 | 231.37 | 211.51 | 234.98 | 214.73 |
| 02-Feb-10 | 229.31 | 213.70 | 232.79 | 217.31 |
| 03-Feb-10 | 228.79 | 213.06 | 231.89 | 215.77 |
| 04-Feb-10 | 226.73 | -- | 232.53 | -- |
| 05-Feb-10 | 227.24 | -- | 230.73 | -- |
| 06-Feb-10 | 224.66 | 203.51 | 228.28 | 211.38 |
| 07-Feb-10 | 226.86 | 213.06 | 230.08 | 216.67 |
| 08-Feb-10 | 234.60 | 213.06 | 242.08 | 217.31 |
| 09-Feb-10 | 237.56 | 212.54 | 244.14 | 218.47 |
| 10-Feb-10 | 231.50 | 213.32 | 238.46 | 214.09 |
| 11-Feb-10 | 231.50 | 214.61 | 234.47 | -- |
| 12-Feb-10 | 232.40 | -- | 237.69 | 216.28 |
| 13-Feb-10 | 235.63 | 219.25 | 237.56 | -- |
| 14-Feb-10 | 234.98 | 222.09 | 232.02 | 216.02 |
| 15-Feb-10 | 232.66 | 215.64 | 231.24 | 214.99 |
| 16-Feb-10 | 233.69 | 215.25 | 232.02 | 215.64 |
| 17-Feb-10 | 233.18 | 213.44 | 230.47 | 211.51 |
| 18-Feb-10 | 231.11 | 209.96 | 228.92 | 212.15 |
| 19-Feb-10 | -- | -- | -- | -- |
| 20-Feb-10 | -- | -- | -- | -- |
| 21-Feb-10 | -- | -- | -- | -- |
| 22-Feb-10 | 228.53 | 211.25 | 231.11 | 215.38 |
| 23-Feb-10 | 231.89 | 212.67 | 235.37 | 216.93 |
| 24-Feb-10 | 226.99 | 209.32 | 229.82 | 211.90 |
| 25-Feb-10 | 227.24 | 207.61 | 229.82 | 211.38 |
| 26-Feb-10 | 225.70 | 208.29 | 230.86 | 211.51 |
| 27-Feb-10 | 226.60 | 212.03 | 230.86 | 215.64 |
| 28-Feb-10 | 226.08 | 211.90 | 230.47 | 215.64 |

17	Voltage Profile of 400 KV sub-sTATIONS in Delhi during FEBUARY 2010

All figures in kV

| Date | 400kV Bamnauli Grid Sub-Station |
| --- | --- |
|  | Max KV | Max Time | Min KV | Min Time | Average KV |
| 01-Feb-10 | 411.30 | 05.04.28 | 378.70 | 10.34.18 | 395.57 |
| 02-Feb-10 | 409.18 | 21.07.24 | 380.81 | 11.06.00 | 394.81 |
| 03-Feb-10 | 407.31 | 21.29.09 | 378.70 | 10.15.59 | 397.54 |
| 04-Feb-10 | 408.95 | 21.00.56 | 374.71 | 09.12.04 | 392.40 |
| 05-Feb-10 | 405.20 | 04.05.10 | 377.29 | 12.07.22 | 392.53 |
| 06-Feb-10 | 408.01 | 20.10.10 | 376.12 | 12.14.38 | 394.49 |
| 07-Feb-10 | 412.47 | 20.53.43 | 389.25 | 11.26.58 | 401.35 |
| 08-Feb-10 | 426.07 | 23.46.11 | 390.89 | 06.08.16 | 404.41 |
| 09-Feb-10 | 430.76 | 01.35.08 | 388.08 | 18.44.27 | 409.96 |
| 10-Feb-10 | 420.44 | 03.06.25 | 390.43 | 06.18.17 | 403.45 |
| 11-Feb-10 | 419.27 | 02.08.19 | 391.60 | 08.12.22 | 404.20 |
| 12-Feb-10 | 418.56 | 04.07.02 | 382.22 | 08.58.11 | 403.45 |
| 13-Feb-10 | 418.56 | 05.04.07 | 388.55 | 09.35.56 | 403.73 |
| 14-Feb-10 | 414.81 | 03.02.59 | 388.78 | 08.40.03 | 404.40 |
| 15-Feb-10 | 413.41 | 04.03.37 | 384.33 | 09.37.44 | 400.44 |
| 16-Feb-10 | 415.05 | 03.05.33 | 385.27 | 12.08.16 | 400.67 |
| 17-Feb-10 | 412.47 | 04.00.33 | 378.23 | 10.24.39 | 398.64 |
| 18-Feb-10 | 408.95 | 04.02.26 | 379.40 | 11.18.52 | 396.94 |
| 19-Feb-10 | -- | -- | -- | -- | -- |
| 20-Feb-10 | -- | -- | -- | -- | -- |
| 21-Feb-10 | -- | -- | -- | -- | -- |
| 22-Feb-10 | 413.87 | 21.56.41 | 376.12 | 10.12.55 | 399.88 |
| 23-Feb-10 | 421.61 | 04.02.16 | 387.61 | 14.42.55 | 402.55 |
| 24-Feb-10 | 411.30 | 04.05.47 | 380.34 | 14.07.01 | 396.24 |
| 25-Feb-10 | 411.30 | 04.03.20 | 375.89 | 12.45.18 | 393.60 |
| 26-Feb-10 | 412.47 | 20.59.28 | 379.64 | 08.11.35 | 395.08 |
| 27-Feb-10 | 411.53 | 03.06.49 | 386.20 | 12.19.40 | 398.88 |
| 28-Feb-10 | 411.30 | 17.35.18 | 384.56 | 12.23.29 | 399.57 |

| Date | 400kV Bawana Grid Sub-Station |
| --- | --- |
|  | Max KV | Max Time | Min KV | Min Time | Average KV |
| 01-Feb-10 | 413.41 | 05.04.18 | 382.69 | 10.15.17 | 398.61 |
| 02-Feb-10 | 412.00 | 21.07.14 | 384.33 | 11.06.00 | 397.71 |
| 03-Feb-10 | 409.89 | 21.28.59 | 382.92 | 10.15.39 | 400.78 |
| 04-Feb-10 | 412.23 | 21.01.06 | 379.17 | 09.12.04 | 395.41 |
| 05-Feb-10 | 407.31 | 20.59.06 | 380.58 | 12.07.52 | 395.44 |
| 06-Feb-10 | 411.53 | 20.10.10 | 379.64 | 12.15.08 | 397.83 |
| 07-Feb-10 | 415.75 | 20.53.43 | 393.24 | 11.24.38 | 404.77 |
| 08-Feb-10 | 428.41 | 23.46.51 | 395.12 | 06.07.56 | 407.89 |
| 09-Feb-10 | 433.10 | 01.34.38 | 392.07 | 18.44.37 | 413.14 |
| 10-Feb-10 | 422.79 | 03.06.15 | 394.41 | 06.18.07 | 406.55 |
| 11-Feb-10 | 421.85 | 02.08.29 | 395.58 | 08.12.32 | 407.31 |
| 12-Feb-10 | 420.21 | 04.03.41 | 386.20 | 08.57.51 | 406.11 |
| 13-Feb-10 | 420.44 | 05.03.47 | 391.60 | 10.12.59 | 406.74 |
| 14-Feb-10 | 417.86 | 03.02.39 | 393.47 | 08.40.23 | 407.30 |
| 15-Feb-10 | 415.52 | 04.01.37 | 388.55 | 09.37.44 | 403.58 |
| 16-Feb-10 | 416.92 | 03.04.43 | 388.78 | 12.08.26 | 403.82 |
| 17-Feb-10 | 414.58 | 04.01.23 | 383.86 | 10.25.19 | 401.48 |
| 18-Feb-10 | 412.00 | 20.57.49 | 383.39 | 11.18.52 | 400.43 |
| 19-Feb-10 | -- | -- | -- | -- | -- |
| 20-Feb-10 | -- | -- | -- | -- | -- |
| 21-Feb-10 | -- | -- | -- | -- | -- |
| 22-Feb-10 | 416.69 | 21.56.41 | 384.09 | 10.13.15 | 403.01 |
| 23-Feb-10 | 423.72 | 01.23.14 | 390.89 | 14.55.46 | 405.68 |
| 24-Feb-10 | 413.87 | 03.31.26 | 384.33 | 14.10.41 | 400.11 |
| 25-Feb-10 | 413.87 | 04.02.10 | 379.17 | 14.16.21 | 397.13 |
| 26-Feb-10 | 415.52 | 20.58.27 | 384.09 | 08.10.55 | 398.74 |
| 27-Feb-10 | 414.34 | 03.07.09 | 389.72 | 12.19.40 | 402.26 |
| 28-Feb-10 | 414.58 | 17.34.58 | 387.61 | 12.23.39 | 402.94 |

18	Details of Lumped Capacitors at nearest 220 kV substation

a)	Delhi Transco Limited (DTL)

| Name of the Sub-stn | Voltage (KV) | Installed Capacity (MVAR) | Working Capacity (MVAR) | Remarks |
| --- | --- | --- | --- | --- |
| Patparganj | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
| Kashmere Gate | 11 | 5.04 | 5.04 |  |
| Gazipur | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Okhla | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
| Lodhi Road | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.976 | 0 | TEMPORARILY DISMANTLED ON 11.11.2006 FOR TAKING OUT 100MVA PR. TX.-I |
| Sarita Vihar | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Vasant Kunj | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Mehrauli | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Najafgarh | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Narela | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |

| Name of the sub-stn | Voltage (KV) | Installed Capacity (MVAR) | Working Capacity (MVAR) | Remarks |
| --- | --- | --- | --- | --- |
| Shalimar Bagh | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 6 | 6 |  |
| Rohini | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 6 | 6 |  |
| Gopalpur | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
| Subzi Mandi | 11 | 6 | 6 |  |
| Kanjhawala | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Park Street | 66 | 20 | 20 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
| Papankalan-I | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Naraina | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
|  | Total Capacity | 749.496 | 743.700 |  |

B.        IPGCL

| Name of the Sub-stn | Voltage (KV) | Installed Capacity (MVAR) | Working Capacity (MVAR) | Remarks |
| --- | --- | --- | --- | --- |
| IP | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 0 | OUT SINCE 08.04.2005. CELLS DAMAGED, ORDER PLACED ON BHEL |
| RPH | 11 | 5.04 | 5.04 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | Total Capacity | 65.04 | 55.04 |  |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 1 | IP STATION |  | 30 |  | 30 |
| 1 | Kamla Market |  |  | 9.65 | 9.65 |
| 2 | Minto Road |  |  | 5.45 | 5.45 |
| 3 | GB Pant Hosp |  |  | 5.45 | 5.45 |
| 4 | Delhi Gate |  |  | 10.9 | 10.9 |
| 5 | Tilakmarg |  |  | 5.04 | 5.04 |
| 6 | Electric Lane |  |  | 5.04 | 5.04 |
| 7 | Connaught Place |  |  | 10.08 | 10.08 |
| 8 | Kilokri |  | 10 | 10.48 | 20.48 |
| 9 | NDSE |  |  | 5.04 | 5.04 |
| 10 | AIIMS |  | 10 | 5.04 | 15.04 |
| 11 | Nizamuddin |  |  | 5.04 | 5.04 |
| 12 | Exhibition-I |  | 10 |  | 10 |
| 13 | Exhibition-II |  |  |  |  |
| 14 | Defence Colony |  |  | 10.9 | 10.9 |
| 15 | IG Stadium |  | 10 |  | 10 |
| 16 | Lajpat Nagar |  |  | 5.04 | 5.04 |
|  | Total |  |  |  | 163.15 |
| 2 | IP Extn. |  |  |  |  |
| 1 | School Lane |  |  | 5.04 | 5.04 |
| 2 | Scindia House |  |  | 5.04 | 5.04 |
| 3 | Vidyut Bhawan |  |  | 15.12 | 15.12 |
| 4 | Nirman Bhawan |  |  | 5.04 | 5.04 |
| 5 | Dalhousie Road |  |  | 5.04 | 5.04 |
|  | Total |  |  |  | 35.28 |
| 3 | RPH Station |  | 20 | 5.04 | 25.04 |
| 1 | Lahori Gate |  |  | 10.45 | 10.45 |
| 2 | Jama Masjid |  |  | 5.03 | 5.03 |
| 4 | Kamla Market |  |  | 5.45 | 5.45 |
| 5 | Minto Road |  |  | 5.45 | 5.45 |
| 6 | GB Pant Hosp |  |  | 5.03 | 5.03 |
| 7 | IG Stadium |  |  | 5.45 | 5.45 |
| 8 | IP Estate |  |  | 10.9 | 10.9 |
|  | Total |  |  |  | 72.8 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 4 | Parkstreet S/stn | 20 | 20 |  | 40 |
| 1 | Shastri Park |  | 10 | 5.45 | 15.45 |
| 2 | Faiz Road |  |  | 10.9 | 10.9 |
| 3 | Motia Khan |  |  | 16.3 | 16.3 |
| 4 | Parshad Nagar |  |  | 16.3 | 16.3 |
| 5 | Anand Parbat |  |  | 10.8 | 10.8 |
| 6 | Shankar Road |  |  | 5.04 | 5.04 |
| 7 | Rama Road |  |  | 14.4 | 14.4 |
| 8 | Baird Road |  |  | 10.08 | 10.08 |
| 9 | Hanuman Road |  |  | 5.04 | 5.04 |
| 10 | Pusa |  |  | 7.2 | 7.2 |
| 11 | Ridge Valley |  |  |  |  |
| 12 | SJ Airport |  |  | 5.04 | 5.04 |
| 13 | B. D. Marg |  |  |  |  |
|  | Total |  |  |  | 156.55 |
| 5 | Naraina S/stn |  | 20 | 5.04 | 25.04 |
| 1 | DMS |  |  | 10.45 | 10.45 |
| 2 | Mayapuri |  | 10 | 5 | 15 |
| 3 | Inderpuri |  | 10 | 5.04 | 15.04 |
| 4 | Rewari line |  |  | 7.2 | 7.2 |
| 5 | Khyber Lane |  | 10 |  | 10 |
| 6 | Kirbi Place |  |  | 5 | 5 |
| 7 | Payal Cinema |  |  | 14.4 | 14.4 |
|  | Total |  |  |  | 102.13 |
| 6 | Mehrauli S/stn | 80 |  | 5.04 | 85.04 |
| 1 | Adchini |  |  | 15.12 | 15.12 |
| 2 | Andheria Bagh |  |  | 10.85 | 10.85 |
| 3 | IIT |  |  | 10.9 | 10.9 |
| 4 | JNU |  | 10 | 10.08 | 20.08 |
| 5 | Bijwasan |  |  | 10.08 | 10.08 |
| 6 | DC Saket |  | 10 | 4.54 | 14.54 |
| 7 | Malviya Nagar | 20 |  |  | 20 |
| 8 | C Dot |  |  |  |  |
| 9 | Vasant kunj B-Blk | 20 |  | 10.9 | 30.9 |
| 10 | Vasant kunj C-Blk | 20 |  | 5.45 | 25.45 |
| 11 | Palam |  |  |  |  |
| 12 | IGNOU |  |  |  |  |
| 13 | R. K. Puram-I |  |  | 10.08 | 10.08 |
| 14 | Vasant Vihar |  |  | 10.08 | 10.08 |
| 15 | Bhikaji Cama Place |  | 10 | 10.08 | 20.08 |
|  | Total |  |  |  | 283.2 |
| 7 | Vasantkunj S/stn | 40 |  | 5.04 | 45.04 |
| 2 | R. K. Puram-II |  |  | 3.6 | 3.6 |
| 4 | Vasant kunj C-Blk |  |  | 5.04 | 5.04 |
| 5 | Vasant kunj D-Blk | 20 |  | 10.25 | 30.25 |
| 8 | Race Course |  |  | 5.04 | 5.04 |
| 9 | Bapu Dhaam |  |  | 5.04 | 5.04 |
| 10 | Nehru Park |  |  | 5.04 | 5.04 |
| 12 | Ridge Valley |  |  |  |  |
|  | Total |  |  |  | 99.05 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 8 | Okhla S/stn | 60 | 10 | 5.04 | 75.04 |
| 1 | Balaji |  |  | 7.2 | 7.2 |
| 2 | East of Kailash |  |  | 10 | 10 |
| 3 | Alaknanda |  |  | 10.85 | 10.85 |
| 4 | Malviya Nagar |  | 20 | 10.49 | 30.49 |
| 5 | Masjid Moth |  |  | 15.94 | 15.94 |
| 6 | Nehru Place |  |  | 21.35 | 21.35 |
| 7 | Okhla Ph-I | 20 |  | 10.9 | 30.9 |
| 8 | Okhla Ph-II |  | 20.93 | 10.49 | 31.42 |
| 9 | Shivalik |  |  | 10.9 | 10.9 |
| 10 | Batra |  |  | 15.8 | 15.8 |
| 11 | VSNL |  |  | 10.8 | 10.8 |
| 12 | Siri Fort |  |  | 10.49 | 10.49 |
| 13 | Tuglakabad |  |  | 10.8 | 10.8 |
|  | Total |  |  |  | 291.98 |
| 9 | Lodhi Road S/stn |  | 20 |  | 20 |
| 1 | Defence Colony |  |  |  |  |
| 2 | Hudco |  |  | 10.9 | 10.9 |
| 4 | Lajpat Nagar |  |  | 5.04 | 5.04 |
| 5 | Nizamuddin |  |  | 5.45 | 5.45 |
| 6 | Vidyut Bhawan |  |  | 10.08 | 10.08 |
| 7 | Kidwai Nagar |  |  | 5.04 | 5.04 |
| 8 | Ex. Gr. II |  |  |  |  |
| 9 | IHC |  |  |  |  |
|  | Total |  |  |  | 56.51 |
| 10 | Sarita Vihar S/stn | 20 |  | 5.04 | 25.04 |
| 1 | Sarita Vihar |  |  | 10.08 | 10.08 |
| 2 | MCIE |  |  | 10.06 | 10.06 |
| 3 | Mathura Road | 20 |  | 5.04 | 25.04 |
| 4 | Jamia Millia |  |  | 5.4 | 5.4 |
| 5 | Sarai Julena |  | 10 | 10.9 | 20.9 |
|  | Total |  |  |  | 96.52 |
| 11 | Wazirabad |  |  |  |  |
| 1 | Bhagirathi |  | 10 | 10.9 | 20.9 |
| 2 | Ghonda | 20 | 20 | 15.94 | 55.94 |
| 3 | Seelam Pur |  | 10 | 21.39 | 31.39 |
| 4 | Dwarkapuri |  |  | 10.06 | 10.06 |
| 5 | Nandnagri | 20 |  | 16.35 | 36.35 |
| 6 | Yamuna Vihar |  |  | 10.8 | 10.8 |
| 7 | East of Loni Road |  |  | 10.8 | 10.8 |
| 8 | Shastri Park |  |  | 10.9 | 10.9 |
| 9 | Karawal Nagar |  |  | 5.4 | 5.4 |
|  | Total |  |  |  | 192.54 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 12 | Geeta Colony |  |  |  |  |
| 1 | Geeta Colony |  |  | 10.49 | 10.49 |
| 2 | Kanti Nagar |  |  | 10.9 | 10.9 |
| 3 | Kailash Nagar |  |  | 15.48 | 15.48 |
| 4 | Seelam Pur |  |  |  |  |
| 5 | Shakar Pur |  |  |  |  |
|  | Total |  |  |  | 36.87 |
| 13 | Gazipur S/stn | 40 |  | 5.04 | 45.04 |
| 1 | Dallupura | 20 |  | 10.9 | 30.9 |
| 2 | Vivek Vihar |  |  | 9.57 | 9.57 |
| 3 | GT Road |  |  | 10.85 | 10.85 |
| 4 | Kondli | 20 |  | 10.45 | 30.45 |
| 5 | MVR-I |  |  | 10.9 | 10.9 |
| 6 | MVR-II | 20 |  | 10.9 | 30.9 |
| 7 | PPG Ind. Area |  |  | 10.06 | 10.06 |
|  | Total |  |  |  | 178.67 |
| 14 | Patparganj S/stn | 40 | 20 | 5.04 | 65.04 |
| 1 | GH-I | 20 |  | 10.45 | 30.45 |
| 2 | GH-II | 20 |  | 10.9 | 30.9 |
| 3 | CBD |  | 10 | 14.94 | 24.94 |
| 4 | Guru Angad Nagar |  |  | 15.49 | 15.49 |
| 5 | Karkadooma |  | 10 | 10.44 | 20.44 |
| 6 | Preet Vihar |  |  | 10.07 | 10.07 |
| 7 | CBD-II |  |  | 7.2 | 7.2 |
| 8 | Shakarpur |  |  | 5.4 | 5.4 |
| 9 | Jhilmil |  |  | 9 | 9 |
| 10 | Dilshad Garden | 20 |  | 16.35 | 36.35 |
| 11 | Khichripur | 20 |  | 10.49 | 30.49 |
| 12 | Mother Dairy |  |  |  |  |
| 13 | Scope Building |  |  |  |  |
| 14 | Vivek Vihar |  |  |  |  |
|  | Total |  |  |  | 285.77 |
| 15 | Najafgarh S/stn | 60 |  | 5.04 | 65.04 |
| 1 | A4 Paschim Vihar |  |  | 10.9 | 10.9 |
| 2 | Nangloi | 20 |  | 15.85 | 35.85 |
| 3 | Nangloi W/W | 20 |  | 5.45 | 25.45 |
| 4 | Pankha Road |  |  | 15.69 | 15.69 |
| 5 | Jaffarpur |  |  | 15.49 | 15.49 |
| 7 | Sagarpur |  |  | 15.9 | 15.9 |
| 8 | Paschimpuri |  | 10 | 15.53 | 25.53 |
| 9 | Paschim Vihar | 40 |  | 15.44 | 55.44 |
| 10 | Mukherjee Park |  |  | 15.49 | 15.49 |
| 11 | Udyog Nagar |  |  | 10.08 | 10.08 |
| 12 | Choukhandi |  |  | 10.08 | 10.08 |
|  | Total |  |  |  | 300.94 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 16 | Pappankalan-I S/stn | 20 |  | 5.04 | 25.04 |
| 1 | Bindapur | 20 |  | 15.9 | 35.9 |
| 2 | Bodella-I | 20 |  | 15.9 | 35.9 |
| 3 | Bodella-II | 20 |  | 14.53 | 34.53 |
| 4 | DC Febakpuri |  |  | 10.04 | 10.04 |
| 5 | G-2 PPK (Nasirpur) |  |  | 10.9 | 10.9 |
| 6 | G-5 PPK (Matiala) |  |  | 15.53 | 15.53 |
| 7 | G-6 PPK |  |  | 5.45 | 5.45 |
| 8 | Harinagar | 20 |  | 10.49 | 30.49 |
|  | Total |  |  |  | 203.78 |
| 17 | BBMB Rohtak Road |  |  |  |  |
| 1 | S.B. Mill |  |  | 10.08 | 10.08 |
| 1 | GTK Road |  |  | 12.64 | 12.64 |
| 1 | Ram Pura |  |  | 12.25 | 12.25 |
| 1 | Rohtak Road |  |  | 10.08 | 10.08 |
| 1 | Vishal |  | 10 | 5 | 15 |
| 1 | Madipur |  |  | 10.43 | 10.43 |
| 1 | Sudershan Park |  |  | 10.99 | 10.99 |
|  | Total |  |  |  | 81.47 |
| 18 | Shalimarbagh S/stn |  | 40 | 6 | 46 |
| 1 | S.G.T. Nagar |  |  | 13.15 | 13.15 |
| 2 | Wazirpur-1 |  |  | 18.8 | 18.8 |
| 3 | Wazirpur-2 |  |  | 14.4 | 14.4 |
| 4 | Shalimarbagh |  |  | 5.44 | 5.44 |
| 5 | Ashok Vihar |  |  | 20.47 | 20.47 |
| 6 | Rani Bagh |  |  | 14.4 | 14.4 |
| 7 | Haiderpur |  |  | 13.15 | 13.15 |
| 8 | SMB Fsc |  |  | 7.2 | 7.2 |
|  | Total |  |  |  | 153.01 |
| 19 | Subzimandi S/stn |  |  | 6 | 6 |
| 1 | Shakti Nagar |  |  | 5.04 | 5.04 |
| 2 | Gulabibagh |  |  | 7.32 | 7.32 |
| 3 | Shahzadabagh |  |  | 18.19 | 18.19 |
| 4 | Tripolia |  |  | 14.4 | 14.4 |
| 5 | B. G. Road |  |  |  |  |
|  | Total |  |  |  | 50.95 |
| 20 | Narela S/stn | 40 |  | 5.04 | 45.04 |
| 1 | A-7 Narela |  |  | 14.4 | 14.4 |
| 2 | AIR Kham pur |  |  | 13.15 | 13.15 |
| 3 | Badli | 20 |  | 5.95 | 25.95 |
| 4 | DSIDC Narela-1 | 20 |  | 5.95 | 25.95 |
| 5 | DSIDC Narela-2 |  |  | 14.4 | 14.4 |
| 6 | Jahangirpuri |  |  |  |  |
|  | Total |  |  |  | 138.89 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 21 | Gopalpur S/stn |  | 30 | 5.04 | 35.04 |
| 1 | Azad Pur |  |  | 21.6 | 21.6 |
| 2 | Hudson Lane |  |  | 5.95 | 5.95 |
| 3 | Wazirabad |  |  | 7.2 | 7.2 |
| 4 | Indra Vihar |  |  | 5.95 | 5.95 |
| 5 | Tri Nagar |  |  | 14.4 | 14.4 |
| 6 | GTK Road |  |  | 12.64 | 12.64 |
| 7 | Jahangirpuri | 20 | 20 | 5.95 | 45.95 |
| 8 | DIFR |  |  | 7.2 | 7.2 |
| 8 | Civil lines |  |  |  |  |
|  | Total |  |  |  | 155.93 |
| 22 | Rohini S/stn | 40 |  | 6 | 46 |
| 1 | Rohini Sec-22 |  |  | 14.4 | 14.4 |
| 2 | Rohini Sec-23 | 20 |  | 5.95 | 25.95 |
| 3 | Rohini Sec-24 |  |  | 7.2 | 7.2 |
| 4 | Rohini-1 |  |  | 5.95 | 5.95 |
| 5 | Rohini-2 |  |  | 13.15 | 13.15 |
| 6 | Rohini-3 |  |  | 5.95 | 5.95 |
| 7 | Rohini-4 |  |  | 11.9 | 11.9 |
| 8 | Rohini-5 |  |  | 13.15 | 13.15 |
| 9 | Rohini-6 | 20 |  | 5.95 | 25.95 |
| 10 | Mangolpuri-1 |  |  | 20.35 | 20.35 |
| 11 | Mangolpuri-2 | 20 |  | 6 | 26 |
| 12 | Saraswati Garden |  |  | 11.9 | 11.9 |
| 13 | Pitam Pura-1 | 20 |  | 12.6 | 32.6 |
| 14 | Pitam Pura-2 |  |  | 12.24 | 12.24 |
| 15 | Pitam Pura-3 |  |  | 7.32 | 7.32 |
|  | Total |  |  |  | 280.01 |
| 23 | Kanjhawala S/stn | 20 |  | 5.04 | 25.04 |
| 1 | Bawana Clear Water |  |  | 14.64 | 14.64 |
| 2 | Pooth Khoord |  |  | 7.2 | 7.2 |
|  | Total |  |  |  | 46.88 |
| 24 | BAWANA S/stn |  |  |  |  |
| 1 | Bawana S/stn No. 6 |  |  | 14.64 | 14.64 |
| 2 | Bawana S/stn No. 7 |  |  | 7.2 | 7.2 |
|  | Total |  |  |  | 21.84 |
| 25 | Kashmeregate |  |  | 5.04 | 5.04 |
| 1 | Civil lines |  |  | 12 | 12 |
| 2 | Town Hall |  |  | 10.49 | 10.49 |
| 3 | Fountain |  |  | 5.45 | 5.45 |
|  | Total |  |  |  | 32.98 |
| 26 | Pappankalan-II |  |  |  |  |
| 1 | DMRC-I |  |  |  |  |
| 2 | DMRC-II |  |  |  |  |
|  | Total |  |  |  | 0 |

20	DETAILS OF BREAK-DOWNS

| SLno | Occurrence of Break-down | details of the Breakdown | TIME OF RESTORATION | Remarks |
| --- | --- | --- | --- | --- |
|  | Date | Time |  | Date | time |  |
| 01 | 01.02.10 | 07.15 | 400KV BAWANA – BAHADURGARH CKT. | 01.02.10 | 09.46 | CKT. TRIPPED ON CB TROUBLE ALARM, CB TC-II FAULTY, T.C-II FAILURE, CB TC-I FAULTY, 295CA, 295CB,, 295CC, CARRIER 30CH-II, 185A-2C, 195CB, 195CC, CB-552 - `Y’ POLE OIL LEAKAGE, hydraulic pressure lock out |
| 02 | 01.02.10 | 16.58 | 220KV GEETA COLONY – PATPARGANJ CKT-II | 01.02.10 | 18.20 | CKT. TRIPPED ON DIST PROT ZONE-I AT GEETA OLONY. |
| 03 | 05.02.10 | 15.56 | 220kv maharani bagh – pragati ckt. | 05.02.10 | 16.22 | ckt. tripped on dist prot `r’ phase zone-i at maharani bagh and on active group-i, dist prot `abc’ phase zone-i at pragati |
| 04 | 05.02.10 | 15.56 | 220kv sarita vihar – pragati ckt. | 05.02.10 | 16.27 | ckt. tripped on dist prot `ac’ phase zone-i at sarita vihar and on 30c, half compressure ac faul at pragati. |
| 05 | 05.02.10 | 15.56 | 220/66kv 160mva pr. tr. at pragati | 05.02.10 | 16.06 | tr. tripped on 86 |
| 06 | 05.02.10 | 15.56 | 220/66kv 100mva pr. tr. at pragati | 05.02.10 | 16.41 | tr. tripped on 86 |
| 07 | 05.02.10 | 15.59 | 220kv pragati – park street ckt-i & ii | 05.02.10 | 16.02 | supply failed from pragati. no tripping at park street. |
| 08 | 06.02.10 | 10.37 | 220kv wazirabad – geeta colony ckt-i | 06.02.10 | 10.48 | ckt. tripped on dist prot `abc’ phase zone-i at geeta colony. |
| 09 | 06.02.10 | 10.37 | 220kv wazirabad – geeta colony ckt-ii | 06.02.10 | 16.08 | ckt tripped on gsc stf wl2, zm-1 trip, zm-2 trip, zm3 start, dist prot at wazirabad. ckt. tried to close at 10.43hrs. but did not hold. jumper found opened near metro station, shastri park. |
| 10 | 06.02.10 | 10.37 | 220/66kv 100mva pr. tr.-iii at wazirabad | 06.02.10 | 18.25 | tr. tripped on e/f |
| 11 | 06.02.10 | 10.37 | 220kv patparganj – geeta colony ckt-i & ii | 06.02.10 | 10.53 | both cktS tripped on 186. ckt-i&ii charged at 10.48. & 10.53hrs respectively. |
| 12 | 06.02.10 | 13.18 | 220/33kv 100mva pr. tr-i & iv at patparganj | 06.02.10 | 13.24 | tr.-i tripped on 86, o/c and tr.-iv tripped on 86, e/f along with 33kv i/c-ii which tripped on o/c, e/f. |
| 13 | 07.02.10 | 08.23 | 66/11kv 20mva pr. tr.-i at najafgarh | 07.02.10 | 08.50 | tr. tripped on 86 along with 11kv o/g pumping stn. feeder which tripped on e/f |
| 14 | 08.02.10 | 13.52 | 220kv gopalpur – subzi mandi ckt-i | 08.02.10 | 14.18 | ckt. tripped on dist prot `ryb’ ph. zone-i at gopalpur. no tripping at subzi mandi. |
| 15 | 08.02.10 | 14.42 | 220kv gopalpur – subzi mandi ckt-ii | 08.02.10 | 15.45 | ckt. tripped on dist prot `ryb’ phase at gopalpur. |
| 16 | 08.02.10 | 14.46 | 220kv gopalpur – subzi mandi ckt-i | 08.02.10 | 16.27 | ckt. tripped on dist prot `ryb’ phase at gopalpur. no tripping at subzi mandi. |
| 17 | 09.02.10 | 00.30 | 400kv bawana – hissar ckt. | 09.02.10 | 06.37 | ckt. tripped on facia cb auto trip, direct trip received, 86, 186a&B, timer 2/aa at bawana. |
| 18 | 09.02.10 | 02.07 | 220kv bamnauli - pappankalan-i ckt-i | 09.02.10 | 11.50 | ckt.tripped on dist prot `b’ ph, 186a&b, cb autotrip at bamnauli. no tripping at pappankalan-i. `y’ ph la damaged at bamnauli end. |
| 19 | 09.02.10 | 02.07 | 220kv bamnauli – najafgarh ckt-i | 09.02.10 | 02.15 | ckt. tripped on dist prot `b’ phase, 186 at najafgarh. |
| 20 | 09.02.10 | 02.55 | 220kv btps – mehrauli ckt-ii | 09.02.10 | 18.49 | ckt. tripped on dist prot `abc’ phase zone-i at mehrauli. |
| 21 | 09.02.10 | 02.55 | 220kv btps – okhla ckt ii | 09.02.10 | 17.05 | ckt. tripped on dist prot `anz-i at okhla. |
| 22 | 09.02.10 | 03.15 | 220/66kv 100mva pr. tr.-i at patparganj | 12.02.10 | 12.55 | tr. tripped on 95ca, 95cc, 86, 87 alongwith 66kv i/c-i which tripped without indication. |
| 23 | 10.02.10 | 11.45 | 400kv mandola – bawana ckt-ii | 10.02.10 | 19.37 | ckt. tripped on dist prot `a’ ph zone-i, e/f at bawana and on `r’ ph. e/f at mandola. |
| 24 | 14.02.10 | 16.13 | 220kv gopalpur – subzi mandi ckt-ii | 14.02.10 | 16.32 | ckt. tripped on dist prot `ryb’ ph. zone-i at gopalpur. no tripping at subzi mandi. |
| 25 | 14.02.10 | 17.23 | 220kv gopalpur – subzi mandi ckt-i | 14.02.10 | 17.39 | ckt. tripped on dist prot `ryb’ ph. zone-i at gopalpur. no tripping at subzi mandi. |
| 26 | 14.02.10 | 17.38 | 220kv mandola – wazirabad ckt-i, ii & iii | 14.02.10 | 18.35 | ckt-i & ii tripped on dist prot `b’ phase zone-iii and ckt-i tripped on dist prot `b’ phase zone-i at mandola. no tripping at wazirabad end. ckt-i, ii & iii charged at 18.35Hrs, 18.35hrs, 18.30hrs respectively. |
| 27 | 14.02.10 | 17.38 | 220kv wazirabad – kashmiri gate ckt-i & ii | 14.02.10 | 18.45 | ckt-i tripped on e/f, 67n, l2g and ckt-ii tripped on directional e.f, 67n at wazira bad. no tripping at kashmiri gate. |
| 28 | 14.02.10 | 17.38 | 220/66kv 100mva pr. tr.-i, ii & iii at wazirabad | 14.02.10 | 18.43 | tr.-i, ii & iii tripped on e/f alongwith 66kv i/c-i, ii & iii. 66kv i/c-i & ii tripped on 86 and 66kv i/c-iii tripped without indication. tr.-i, ii & iii charged at 18.43hrs. |
| 29 | 14.02.10 | 17.38 | 220kv wazirabad – geeta colony ckt-i & ii | 14.02.10 | 19.09 | following tripping occurred : at geeta colony wazirabad ckt-i:dist prot `abc’ ph zone-ii main-1 : disty prot `c’ phase zone-i, main-ii : ob, start nc wazirabad ckt-ii: active group-i, dist prot `abc’phase, 27ryb, 86 main-ii : dist prot `abc’ phase zone-i, 38y ckt.-i & ii charged at 19.09hrs. and 18.49hrs. respectively. |
| 30 | 14.02.10 | 17.38 | 220kv patparganj – geeta colony ckt-ii | 14.02.10 | 17.58 | ckt. tripped on under frequency, 86 at patparganj. |
| 31 | 14.02.10 | 17.38 | 220/33kv 50mva pr. tr.-ii and 220/33kv 100mva pr. tr.-iv at patparganj | 14.02.10 | 17.59 | both tXss tripped on ref lv side, 86 along with their 33kv i/cs which tripped on e/f. tr.-ii & iv charged at 17.59hrs. |
| 32 | 14.02.10 | 17.38 | 220kv patparganj – ip ckt-i & ii | 14.02.10 | 17.52 | supply failed from patparganj. no tripping at ip. |
| 33 | 15.02.10 | 09.50 | 220/33kv 100mva pr. tr.-iii at okhla | 15.02.10 | 13.10 | tr. tripped without indication. |
| 34 | 15.02.10 | 16.02 | 220kv gopalpur – subzi mandi ckt-i | 15.02.10 | 17.39 | ckt. tripped on dist prot `ryb’ ph. zone-i at gopalpur. no tripping at subzi mandi. |
| 35 | 15.02.10 | 20.41 | 220kv mandola – wazirabad ckt-i | 15.02.10 | 21.05 | ckt. tripped on dist prot `ryb’ phase zone-i at wazirabad. |
| 36 | 18.02.10 | 14.12 | 220kv wazirabad – kashmiri gate ckt-ii | 18.02.10 | 15.42 | ckt. tripped on dist prot zone-i at wazirabad. no tripping at kashmiri gate |
| 37 | 18.02.10 | 15.43 | 220kv bamnauli – mehrauli ckt-i | 18.02.10 | 16.03 | ckt. tripped on dist prot `r’ phase zone-i, 186a&b at bamnauli and on dist prot zone-i at mehrauli. |
| 38 | 20.02.10 | 14.30 | 220kv wazirabad – kashmiri gate ckt-ii | 20.02.10 | 16.24 | ckt. tripped on general trip gfc stf w1, zm-i trip, zm-2 & zm3 start at wazirabad. no tripping a kashmiri gate. |
| 39 | 21.02.10 | 12.57 | 220kv wazirabad – kashmiri gate ckt-ii | 21.02.10 | 13.15 | ckt. tripped on rxme18, general trip, gfc-stfwl1, gfc-stfwl2 & wl3, zm-1 tripped, m2 start, m3 start at wazirabad. no tripping at kashmiri gate. |
| 40 | 22.02.10 | 15.32 | 220kv mandola – wazirabad ckt-iv | 22.02.10 | 16.08 | ckt. tripped on `ryb’ ph, z1 trip, z2 trip, zm start, zm2 start, fault loop l1-l2 at wazirabad & on dist prot `r-y’ ph. at mandola. |
| 41 | 23.02.10 | 17.34 | 220kv mandola – wazirabad ckt-iv | 24.02.10 | 15.26 | ckt.tripped on dist prot`b’ph. zone-i,86 ryb, 186a&b at mandola and on rxme18, 3 ph.,general trip, ryb ph., dist prot zone-i at wazirabad. ckt. tried to close at 20.23hrs. after getting clearance from line department but did not hold and again tripped on same indication at wazirabad. ckt. finally charged at 15.26hrs. on 24.02.10 |
| 42 | 23.02.10 | 18.15 | 220/66kv 100mva pr. tr.-ii at park street | 23.02.10 | 18.40 | tr. tripped on differential |
| 43 | 24.02.10 | 22.08 | 33/11kv 16mva pr. tr.-ii at subzi mandi | 25.02.10 | 00.27 | tr. tripped on spr/prv, 86, auxiliary relay, 30abc, differential |
| 44 | 24.02.10 | 11.20 | 220kv maharani bagh – pragati ckt. | 24.02.10 | 11.20 | ckt. tripped without indication at maharani bagh. |

21	DETAILS OF UNDERFREQUENCY TRIPPINGS

NIL