|  | पंजीकृत कार्यालय :शक्ति सदन, कोटला रोड़, न्यू दिल्ली-110002 (Regd. Office Shakti Sadan, Kotla Road, New Delhi-110002) कार्यालय उपमहाप्रबंधक (एस.ओ.) Office of Dy. General Manager (SO) एस एल डी सी बिल्डिंग, मिंटो रोड़, न्यू दिल्ली-110002 SLDC Building, Minto Road, New Delhi-110002 Ph: 23221149 FAX No.23221012 |
| --- | --- |
| No. F./DTL/207 )/12-13/DGM(SO)/148 | Dated : 11.06.2012 |

Subject  : 	Minutes of the 6th Meeting of Grid Coordination Committee held on 08.05.2012 at Hotel Connaught, Connaught Place, New Delhi-110001

Dear Sir,   /  महोदय

The Minutes of the 6th Meeting of Grid Coordination Committee held on 08.05.2012 at the Hotel Connaught, Connaught Place, New Delhi-110001 is enclosed for ready reference and further necessary action please.

Thanking you,

भवदीय   /  Yours faithfully

Encl. as above

(उपमहाप्रबंधक (एस.ओ.)/Dy. G. M. (SO)

Convener (GCC)

List of addresses

- General Manager, NRLDC, 18A- SJSM, Katwaria Sarai, New Delhi-110016

- Director (Engg.), DERC, Viniyamak Bhawan, C-Block, Shivalik, New Delhi-110017

- General Manager (Planning), DTL, Shakti Deep Building, Jhandewalan, New Delhi

- Executive Director (Engineering), NTPC, Corporate Centre, EOC Noida, Sector-24, UP-201301-Fax No.0120-2410200

- Chief Executive Officer, Aravali Power Company Pvt. Ltd. 5th Floor, Engineering Office Complex, A-8A, Sec. 24, Noida, 201301 (U.P.)-fax no. 0120-2410361

- Chief Engineer (SO), Punjab SLDC, PSTCL, SLDC Complex, Near 220kV Grid S/Stn Ablowal, Patiala, Punjab-147001, Fax No. 0175-2365340, 0175-2367490

- Chief Engineer (System Operation), Haryana SLDC, HVPNL, Shakti Bhawan, Sector-6, Panchkula-134109, Fax No. 0172-2560622

- General Manager, Bawana CCGT Plant, Sector 5, DSIIDC Indl. Area, Bawana, New Delhi-110039

- General Manager (Commercial), NTPC, Noida Fax No. 95120-24100563

- C.E., Haryana Power Procurement Centre, Panchkula, Haryana, Fax No. 0172-3019169

- General Manager (O&M)-I, DTL, Park Street 220kV Grid S/Stn. New Delhi-110001

- General Manager (O&M)-II, DTL Shakti Deep Building, Jhandewalan, Delhi

- G. M. (SLDC), SLDC Building, Minto Road, New Delhi-110002

- G. M., Badarpur Thermal Power Stn., Badarpur, New Delhi-44

- General Manager, RPH

- CWE (Utilities), MES, Delhi Cantt, New Delhi-110010

- Garrison Engineer (Utilities), MES, Delhi Cantt., New Delhi-110010

- Sh. Chandramohan, Vice President (Network Operation) BRPL, BSES Bhawan, Nehru Place, New Delhi

- Sh. Mukesh Dadhich, Dy. G.M. (SO), BYPL, Balaji Estate, Kalkaji, New Delhi-110019

- Addl. Vice President, System Operation, BRPL, Balaji Estate, Kalkaji, New Delhi

- Chief Engineer (Electrical-I), NDMC, Palika Kendra, New Delhi-110001

- Chief Engineer (Electrical-II), NDMC, Palika Kendra, New Delhi-110001

- Chief Engineer (Transmission System),BBMB, SLDC Complex, Sector-28, Industrial Area Phase-I, Chandigarh.

- Director (Comml.), NDMC, Palika Kendra, New Delhi-110001

- General Manager, GT Station

- General Manager, Pragati Power Corporation Ltd, Pragati Power Station New Delhi

- Sr. G. M. (PM & CC),  Grid S/stn Bldg., Hudson Lane, Kingsway Camp, Delhi-9

- Dy.G.M.(Metering & Prot), Delhi Transco Ltd., Parkstreet,220kV S/Stn, New Delhi-1

- Dy.G.M (Fin)-I, DTL, Shakti Sadan, New Delhi-110002

- Dy. G. M. (Fin-II), DTL, Shakti Sadan, New Delhi-110002

- HOG (Power System and Trading), TPDDL, Cennet Building, Adjacent to 66/11kV Pitampura-3 Grid Building, Near PP Jewellers, Pitampura, Delhi-34.

- Sh. Sanjay Banga, Sr. General Manager (PSC & A), TPDDL, Scada Building, Near Netati Subhash Place Metro Station, Pitampura, Delhi-110034

- Dy.G.M.(O&M)-I, 400kV Bamnauli S/Stn, Najafgarh-Bijwasan Road, Bamnauli, New Delhi

- Dy. G.M.(O&M)-II, DTL, 220kV Park Street Grid S/Stn, near RML Hospital, Park Street, New Delhi-110001

- Dy. G.M. (O&M)-III, DTL, Shakti Deep Building, Jhandewalan, Delhi

- Dy. G.M.(OS), DTL, 220kV Naraina Grid S/Stn, New Delhi-110010

- Sh. Sunil Kakkar, Head (PMG), BSES Yamuna Power Ltd., 2nd Floor, Shakti Kiran Building, Karkardooma, Delhi-110092

- Sh. Sanjay Srivastav, Asstt. Vice President (PMG), BSES Rajdhani Power Ltd, Bldg. No. 20, Nehru Place, New Delhi - 110019

- General Manager (Commercial), National Thermal Power Corporation, NTPC NCR Headquarter, Sector-24, Noida, UP-201301

- DGM(SCADA), Delhi SLDC

- Manager (SO)-Shift, Delhi SLDC

- Executive Engineer (SO), NDMC

Copy for favour of kind information to :-

  - Secretary, DERC, Viniyamak Bhawan, C-Block, Shivalik, New Delhi-110017

  - Chairman and Managing Director, DTL

  - Chairperson, New Delhi Municipal Council, Palika Kendra, Sansad Marg, New Delhi

  - Member Secretary, NRPC, Katwaria Sarai, New Delhi-110016

  - Member (Power Regulations), BBMB, Sector-19B, Madhya Marg, Chandigarh

  - Director (Operations), NTPC, Scope Complex, 7 Institutional Area, Lodhi Road, New Delhi-110003

  - Director (Commercial), NTPC, Scope Complex, 7 Institutional Area, Lodhi Road, New Delhi-110003

  - Director (Projects), NTPC, Scope Complex, 7 Institutional Area, Lodhi Road, New Delhi-110003

  - Managing Director, Haryana Vidyut Prasaran Nigam Ltd, Shakti Bhawan, Sector-6, Panchkula, Haryana-134109

  - Managing Director, Indraprastha Power Generation Company Ltd (IPGCL) / Pragati Power Corporation Ltd (PPCL), Himadri, Rajghat Power House, New Delhi-110002

  - Director (Operations), DTL

  - Director (Finance) DTL

  - CEO, BSES Rajdhani Power Ltd, BSES Bhawan, Nehru Place, New Delhi-110019

  - CEO, BSES Yamuna Power Ltd, Shakti Kiran Building, Karkardooma, New Delhi-92

  - CEO, Power System Operation Corporation (POSOCO), B-9, Qutub Institutional Area, Katwaria Sarai, New Delhi-110016

  - Managing Director, North Delhi Power Ltd, 33kV Grid S/Stn, Hudson Lane, Kingsway Camp, Delhi-110009

  - Chief Engineer(Utilities),CWE, MES, Kotwali Road, Near Gopi Nath Bazar, Delhi Cantt  New Delhi-110010

  - Addl. Secretary (Power), Govt. of NCT of Delhi, Delhi Secretariat, New Delhi

DELHI TRANSCO LTD.

(Regd. Office : Shakti Sadan, Kotla Road, New Delhi 110002)

[Office of Dy. General Manager (SO)]

SLDC Building, Minto Road, New Delhi – 110 002

Phone No.23221149, 23221175, Fax 23221012, 59

Subject :	Summary Record of discussions held in the 6th Meeting of Grid Coordination Committee (GCC) of Delhi, held on 08.05.2012 at Hotel Connaught, Connaught Place, New Delhi-110001

The list of participants is enclosed at Annexure-1.

WELCOME

Sh. A. K. Haldar, Director (Operations), DTL and Chairperson of Delhi Grid Coordination Committee (GCC) welcomed the delegates in the meeting.  In his opening remarks, he mentioned that Grid Coordination Committee (GCC) is the Apex Body as provided in the Clause-6.2 of Delhi Grid Code.  He further informed that the last meeting was held on 25.10.2010 and this meeting is scheduled after the gap of about 1½ year.  It is happy to note that the coordination issues amongst the Stakeholders are almost NIL which is evident from the long gap of meeting of the Grid Coordination Committee.  It is understood that the coordination issues are settled at Sub-Committees’ level and this Grid Coordination Committee meeting was necessitated to approve the important issues such as Protection Plan and Metering Code.  The proceedings also reveal that both the procedures were deliberated at respective Sub-Committees and decided to put up the procedures for approval of GCC.

Agenda also involves the proposed Guidelines for operationalization of Intrastate Open Access in Delhi.  The Committee constituted for framing the guidelines has already submitted the report to DERC to resolve precipitated issue whether to consider open access customers as embedded customer of the Distribution Company or to treat them as separate entities for all practical purposes.  The issue is required to be resolved at the Delhi Electricity Regulatory Commission’s level and it is hoped that the Commission may come up with the solution soon.  However, he mentioned that members are welcomed to offer any further suggestion towards the guidelines when the item is taken up for discussion in the meeting.  It is also very vital in view of latest communication of Govt. of India that all consumers whose load demand is more than 1 MW and above are deemed open access consumers and State Electricity Regulators have no jurisdiction for fixation of the retail tariff of such type of consumers.

From the power supply point of view, he informed that Delhi is one of the best managed States in the Country with regard to availability.  In spite of the power regulations imposed by some of the power supply and transmission agencies during peak winter season following the payment related issues due to adequate arrangements, no power crisis was engulfed the capital due to the shortage.   It was also a note worthy factor that from 27.04.2012, all power regulations have been withdrawn by the concerned agencies.  As far the power supply of summer months are concerned, the anticipated demand is expected to be within the range of 5500MW for which the Distribution Companies have made elaborate arrangements to meet the demand.

He hoped that DTL and Discoms’ respective system are capable to handle such demand during summer months.  It is also note worthy that the generation capacity has also been increased substantially like Bawana (685MW), Jhajjar (1000MW), availability from DVC enhanced from 100/150MW to 500MW apart from long term arrangements for power from Maithon and CLP Jhajjar by TPDDL.   It is also worthwhile to mention that the State-of-the-Art Waste to Energy Plant of generation capacity of 16MW has also been commissioned at Okhla.  This plant not only supplies energy but also efficiently disposes the municipal waste.

Lastly, he thanked IPGCL/PPCL Management to host the meeting.

With above remarks, he advised the Convener to take up the agenda of the meeting.  Subsequently the agenda was taken up and gist of the discussions and decision are as under:-

1	Confirmation of the minutes of 5th meeting of GCC held on 25.10.2010.

The minutes of the 5th meeting of GCC held on 25.10.2010 have been circulated vide letter no. F.DTL/207/2010-11/DGM(SO)/308 dt. 16.11.2010. No comments have been received so far.

GCC confirmed the minutes of the 5th meeting of GCC held on 25.10.2010.

2	Phasing out of Stage-I units of BTPS (95MW X 3).

BTPS representative intimated that the gas allocation has not been made sofar for the proposed Gas Turbine project envisaged as the replacement of Stage-1 (95X3) units of BTPS.

It was also confirmed that no gas can be available for the new Gas projects till 2015-16due to less availability of the same.  They are planning to install the units after 2015-16 when the allocation of gas is expected to be made available.  However, evacuation plan has already been finalized in the 30th Standing Committee Meeting of Power System Planning of Northern Region of CEA on 19.12.2011.  The details are as under:-

Item no. -14: Connectivity of new CCPP-I (1050MW) generation of M/s NTPC Limited at existing Badarpur Thermal Power Station, in Delhi.

POWERGRID informed that NTPC Limited, had applied for connectivity of their new CCPP-I generation(1050MW) coming up in the existing premises of Badarpur Thermal Power Station in Delhi and as per application, connectivity is required by 2013-14. NTPC stated that they could not inform the firm commissioning schedule at present. Badarpur is an existing generating station of NTPC (Stage-I -3X95 MW, Stage-II -2X210 MW). Evacuation of power is at 220kV through five numbers of 220kV D/c lines. For the new CCPP-I generation (1050MW) of NTPC, the step up voltage of the generation is 400kV and nearest substation is existing 220kV Badarpur Thermal Stage-I generation switchyard. It was discussed that Delhi is already facing high short circuit levels. The situation is further aggravated by Right of Way constraint. Hence system studies would be carried out to analyze if the proposed generation can be evacuated with existing/under construction transmission system. Strengthening would be evolved in case of constraint under base case or contingency conditions. The study would be carried after finalizing the commissioning schedule and LTA application is received with requisite information.

NTPC informed that presently they had applied only for connectivity and the same may be granted. Long Term Access may be considered separately by CTU, once Long term Access application is made to CTU.

After discussion, connectivity was agreed by installing 1x315 MVA, 400/220kV ICT at Badarpur to connect proposed generation at 400kV with existing 220kV bus.

- A provision for 1X125 MVAR Reactor would be kept at Generating Station

- M/s NTPC may inform the schedule and apply for LTA

- All Conditions as applicable listed in Annexure –I would be applicable.

DTL’s Planning Department has to closely associate with BTPS authorities for establishment of 400kV S/Stn for evacuation of power from the proposed gas unit as and when it is ready for commissioning as discussed in the above said SCM.

BTPS representative further intimated that to run effectively the stage-1 units, they are required to infuse additional amount about Rs. 268 Crores to enhance the reliability of Stage-I units for 10-12 years for Renovation and Modernization work for which the proposal is under difference stage of technical scrutiny as the replacement plant based on gas fuel maybe delayed beyond 2015-16.

Distribution Licensees opined that before approaching CERC for getting the approval of R&M expenditures for Stage-1 units, the proposal should be discussed along with cost benefit for the consumers of Delhi for such activities in the Coordination Forum of the beneficiaries.

BTPS representatives agreed for the same.

With regard to power availability from the proposed replacement plant, i.e. 1050MW combined cycle gas units, the representative of TPDDL doubted the availability of power to Delhi.  He mentioned this because of the fact that as per the National Tariff Policy issued by Govt. of India, Discoms are authorized to enter PPAs for purchase of power only through competitive bidding process from 05.01.2011.  Since no PPA has been executed for purchase of power so far from the proposed units, the tariff of the BTPS Station should be of competitive bidding and not on cost plus basis.

SLDC representative queried whether such stipulation is applicable to replacement / expansion scheme of the existing station, TPDDL representative requested BTPS to get the clarification from concerned authorities in this regard.  Other Discoms’ representatives also requested BTPS authorities to do the same.  BTPS representative agreed for obtain the clarification.

Concluding the discussions, the Chair advised BTPS authorities following :-

- Any major expenses to be incurred by BTPS which has the tariff impact should be discussed first with the beneficiaries in the coordination forum before putting up the same for the approval before the concerned Electricity Regulatory Commission.

- The mode of the power procurement by Distribution Companies from the proposed gas units at BTPS through MoU route or competitive bidding is also required to be ascertained.

3	FINALIZATION OF PROTECTION PLAN

General Manager (O&M)-I, DTL clarified the salient features of the Protection Plan proposed to be implemented in Delhi Power System as mentioned by Delhi Grid code (DGC).  It has been clarified that all 66kV and 33kV under ground cables and over head lines upto 1 kilo meter length, main protection shall essentially be numerical current differential protection.  Back up protection is directional over current and earth fault protection.

This is envisaged as the Distance Protection for shorter line is not effective due to over reach problem.

To a query whether it was applicable for all existing system, it was answered that that it is proposed for mainly upcoming system and the existing system should be phased out in a phased manner.

DERC representative informed that the Commission has approved the Capex for current differential relays for the upcoming system for TPDDL.

General Manager, Pragati was of the view that the entire system should have the same protection philosophy and there should have a time bound manner for replacement of the existing scheme to proposed scheme of current differential.

DERC representative informed that if such schemes with proper justification are received, the Commission may consider the same.

After the detailed discussions, Protection Plan approved by the Protection Sub-Committee meeting held on 16.08.2011 has been approved by GCC for implementation.  The approved Protection Plan is placed at Annexure-2.

4	FAULT LEVEL COMPUTATION AT DTL SUB-STATIONS.

In the 5th GCC meeting, held on 25.10.2010 it was explained that the fault level computation is one of the references of protection audit undertaken by CPRI.

General Manager (O&M)-I, has intimated that CPRI has already submitted the report of Protection Audit conducted by them.  The details of the fault level have also been indicated in it.  The Chair enquired any specific observation on the report, it was answered that as per the CPRI study, the fault level in all substations of DTL are within the normal level i.e. order of 15 kAmps.  However, General Manager (O&M)-I cautioned that as per the DR analysis of recent trippings at GT Station, the fault level indications show 24 kAmps fault current.

General Manager, GT also echoed against the findings of CPRI as the fault current in every tripping at GT Station is more than 15kAmps.

Chair advised the O&M-I Department to circulate the report of CPRI to all Stakeholders and discuss the same in the Protection Sub-Committee meeting and specific observations emerging out of such discussions be communicated to CPRI and be taken at RPC level for resolution.

The copy of the report of the CPRI is enclosed as Annexure-3.

5	INSTALLATION 2ND 66/11KV TRANSFORMER AT GAZIPUR SUB-STN.

At the time of inheritance of Gazipur S/Stn by DTL from erstwhile DVB, there was only 66/11kV 20MVA transformer.  As per the norms and for ensuring continuity of supply, the second transformer is also essential.  However, there was a confusion for incurring capital expenditure for the installation of second transformer to feed 11kV System by DTL being the Transmission Utility.

It was informed that similar case of installation of additional 66/11kV transformer at Wazirabad S/Stn went upto DERC for adjudication of the dispute of sharing of cost.

DERC vide its order on petition no. 74/2008 with regard to erection, commissioning and testing of 66/11kV 20MVA Pr. Tr. along with associated equipments at South of Wazirabad 220kV S/Stn. mentioned that DTL and BYPL mutually agreed that DTL will retain the said Transformer and claim the expenditure incurred including carrying cost / interest viz-a-viz capitalization in its ARR with regard to cost the same principle of cost can be applied in respect of installation of 2nd 66/11kV 20MVA Tx. at Gazipur.

BYPL representative requested DTL to install immediately the second transformer as in case of outage of the existing transformer areas fed from the sub-station is getting affected.  He cited a recent incident of the outage of the transformers wherein the load remain affected for more than 7hours.  To avoid the recurrence of such incidence, the second transformer should be commissioned as early as possible as cost sharing is not an issue as settled by DERC in the case of Wazirabad as DTL is entitled for capitalization for the installation of additional transformer.

General Manager (O&M)-II informed that though a 66/11kV 20MVA transformer was transported from Wazirabad-I for the installation the same at Gazipur, the results were not conducive for energization of the same.  Now, it has been decided that the transformer which got repaired at Mehrauli S/Stn be installed at Gazipur.  He assured to get it commissioned by the end of July 2012.

Chair advised the concerned O&M Department to install the transformer as quick as possible preferably by 30th June 2012.

6. 	PROVSIONS OF SPARE TRANSFORMER CAPACITY.

In the last GCC meeting held on 25.10.2010 it was decided to have one spare transformation capacity at all level as hot reserve capacity at DTL’s S/Stn i.e. 400/220kV 315MVA, 220/66kV 160MVA Pr. Tr., 220/66kV 100MVA Pr. Tr., 220/33kV 100MVA Pr. Tr., 66/33kV 30MVA Pr. Tr., 66/11kV 20MVA Pr. Tr. & 33/11kV 20/16MVA Pr. Tr.. The State OCC Meeting is regularly monitoring the hot reserve position. The latest position is as under:-

| S.N | Voltage level | Present population in nos. | Status of the hot reserve |
| --- | --- | --- | --- |
| 1 | 400/220kV, 315MVA ICT, | 10 | One Tx at 400kV Mundka would be hot reserve. Now the transformer has been shifted to Bawana following a break-down there. The transformer which was under break-down is getting repaired and shall be installed at Mundka in hot reserve condition within a period of five months. |
| 2 | 220/66kV, 160MVA Tx | 7 | 160MVA Tx earmerked for 220kV Pappan Kalan-II would be the hot reserve. The installation is taking place and would be completed within three months. |
| 3 | 220/66kV, 100MVA Tx | 42 |  |
| 4 | 220/33kV, 100MVA Tx, | 33 | New Tx. is required to be purchased for hot reserve for which procurement action shall be initiated shortly by Planning Department. DTL’s Planning Department repesentative indicated that three 100MVA transformers were available but due to diversion to various places, at present no hot reserve is available. |
| 5 | 66/33kV 30MVA Tx, | 3 | The 33kV level at Narela is being dedicated for AIR Khampur feeder. Howerver, as per the decision of the Standing Committee, the load is propsed to be transferred to IFSL S/Stn of TPDDL. Thus, the existing Tx. would be hot reserve after the transfer of AIR Khampur load from Narela. TPDDL infomed that the scheme is envisaged for 2014-15. |

| S.N | Voltage level | Present population in nos. | Status of the hot reserve |
| --- | --- | --- | --- |
| 6 | 66/11kV 20MVA Tx | 23 | New Tx. is required to be purchased for hot reserve for which procurement action shall be initiated shortly by Planning Department. |
| 7 | 33/11kV 20/16MVA Tx | 16 | New Tx. is required to be purchased for hot reserve for which procurement action shall be initiated shortly by Planning Department. At present, there is no hot reserve. Due to non availability of Hot Reserve, 220kV Shalimar S/Stn is left with only 33/11kV Tx. since 09.07.2011. The transformer has been obtained from TPDDL on loan basis which is being installed. To a query by TPDDL regarding the energiation of the second 33/11kV transformer at Shalimar Bagh, GM(O&M)-II informed that it would be readied by the end of June 2012. TPDDL requested DTL to expedite early commissioning of the transformer. Chair advised the O&M Department to expedite the commissioning positively by 15.06.2012. The Chair further advised O&M Department to immediately initiate case for purchase of additional transformer to meet such eventualities. |

GCC made very clear that hot reserves indicate all associated equipments along with the transformers on charged condition.  In case of use of the system to meet the eventualities, it should be ensured that the same should be replaced as quick as possible.

Chair further advised the Planning Department of DTL to immediately finalize the scheme for provision of hot reserve as decided in the 5th meeting held on 25.10.2010 in consultation with O&M Departments for finalization of locations for providing hot reserve for each voltage level.

7	Special Protection Scheme to take care of tripping of one of the ICTS at 400kV Sub-Stations.

As per the NRPC decision, DTL has to shed load through SPS at 400kV S/Stns. at Bawana and Bamnauli to take care of the eventuality of tripping of any one of the ICTs. The installation of SPS at Mandola and Maharani Bagh is responsibility of PGCIL.

At Bawana, 220kV Najafgarh & Khanjawala Ckts. should be tripped affecting the load of 250MW to take care of tripping of one ICT.

At Bamnauli, 220kV Najafgarh Ckt. I & II & Naraina Ckt. I & II should be tripped to give the load relief of about 250MW to take care of tripping of one ICT.

The issue was figured in the meeting taken by Joint Secretary (OM), Ministry of Power, Govt. of India on 18.04.2012 which was convened to review the power supply position of summer 2012.  In the meeting, DTL informed that the required network reconfiguration for redistribution of load on Mundka ICT to transfer the load from Bawana and Bamnauli was being done.  Further, it was assured that the load of Maharani Bagh would also be increased to reduce loading on Bawana & Bamnauli ICTs.

G.M. (O&M)-I informed that due to adequate transformation capacity at Maharnai Bagh (1630MVA), there is no possibility of cascade tripping in case of outage of any one of the ICTs.  As such, SPS at Maharani Bagh can be delayed till the picking up of load at Maharani Bagh.  He informed that due to proposed addition of two 315MVA transformers at Bawana, the immediate need of implementation of SPS at Bawana S/Stn can be ruled out.  However, he assured that by 31.05.2012, the SPS would be implemented at Bamnauli S/Stn.

The Chair advised that though the priority of SPS installation be given to Bamnauli but there should not be any lack of speedy installation of SPSs at Bawana and Maharani Bagh S/Stns.  He further cautioned that as per CEA stipulations, the bus split arrangements should be enforced at Bawana for evacuation of Bawana CCGT generation to reduce the fault level.  In bus split operation, all six ICTs will not be operated in parallel and hence SPS is required at Bawana also.

Further, to take care of multiple line outage of Bawana, SPS any way is required to be installed without any slackness.

8 	IMPLEMENTATION OF STATE – OF - THE – ART – LOAD MANAGEMENT SCHEME & UNDER FREQUENCY RELAYS BY DISCOMS

The IEGC stipulates implementation of state of the art load management scheme to avoid lowering of frequency below 49.8Hz. CERC has been regularly monitoring implementation of the scheme. Delhi SLDC has undertaken that the scheme is in place at TPDDL and BSES utilities before CERC in a suo-moto petition in this regard.  NDMC has undertaken that the scheme would be implemented by 31.03.2012 and based on their assurance the same was also intimated to CERC on an Affidavit by Delhi SLDC.

Delhi OCC has also been regularly monitoring the position.

Further, DERC vide its order dated 17.01.2012 in petition no. 16/2008 in the matter of endangering the regional grid security by continuous violation of section 24.1–24.3 of Delhi Electricity Grid Code has directed discoms to put under frequency relays in their respective areas of supply in service latest by 31.03.2012 and compliance of this direction of the commission should be reported latest by 07.04.2012. In the last Delhi OCC meeting held on 29.03.2012 the Discoms intimated that the order of Delhi State Electricity Commission would be complied and copy of the report would be sent to SLDC and DTL in due course. SLDC informed that sofar no has been received from any of the Disoms.

BRPL, BYPL and TPDDL have confirmed that they have given the report to DERC, copy of the same would be provided to SLDC soon.  All Distribution Licensees expressed the fact that the updation of real time scheduling and actual drawal is pre-requisite for proper functioning of the Automatic Load Management Scheme.  They requested SLDC to ensue the real time updation of schedules particularly in the event of exigencies i.e. over drawal of Delhi under low frequency regime.  For accurate actual drawal on real time basis, they emphasized immediate need of Discoms data integration with SLDC.

SLDC representative indicated that the Discom data integration has already been envisaged in ULDC Phase-II implementation.  The completion time would be two years from now.

Sh. Sanjay Banga, Sr. G.M., TPDDL mentioned that they are facing problem in putting the 86 nos. 11kV feeders directly emanating from 33/11kV and 66/11kV transformers installed at DTL’s 220kV Grid S/Stns in the scheme of automatic load regulation scheme.  He requested handing over of these assets for O&M and Control of 33/11kV & 66/11kV transformers and 11kV switchgears installed at DTL’s S/Stns to them.

SLDC representative informed that there are 204 nos. 11kV feeders emanating from DTL’s S/Stn catering a load demand of about 500MW at the time of peak contributing 10% of the peak demand.  He opined that these feeders should also be put in the ambit of automatic load regulation scheme.  However, he mentioned about the statutorily bound Transfer Scheme that upto line isolators of 33kV, 66kV and 11kV, the assets belong to DTL.  As such, the transfer of these assets to other utilities would create legal hurdles.

TPDDL representative requested to consider the issue of bringing the 11kV feeders emanating from DTL’s 220kV S/Stns. at SCADA control of concerned Distribution Companies without handing over the assets without hindering the Transfer Scheme Provisions.  The representative of other Distribution Companies also supported the views of TPDDL.

General Manager (Commercial), DTL opined there should not be any problem to bring the 11kV feeders emanating from the sub-stations of DTL under SCADA control of concerned Distribution companies without transferring the Assets to them.  However, before implementing the scheme, all technical aspects should be taken care for effective operation of the system.

After brief discussions, GCC advised to consider the issue in the next Operation Coordination Committee meeting and final outcome may be placed before GCC for taking a decision with respect to transfer of operational control of 11kV feeders emanating from 220kV Grid S/Stn of DTL to concerned Distribution Licensees.

OPERATIONAL ISSUES

9 	POWER SUPPLY POSITION

SLDC made the presentation on Power Supply and other related issues for Summer 2012 and Winter 2012-13.

Power supply position for the period May 2012 to September 2012 is as under :-

All Figures in MW

| Month | 1st Fortnight | 2nd fortnight |
| --- | --- | --- |
| MAY 2012 | 00-03 | 03-09 | 09-12 | 12-18 | 18-24 | 00-03 | 03-09 | 09-12 | 12-18 | 18-24 |
| DEMAND | 4500 | 4100 | 4500 | 5000 | 4750 | 4700 | 4450 | 4900 | 5300 | 5100 |
| AVAILABILITY | 4969 | 4969 | 4969 | 5116 | 5204 | 5136 | 5136 | 5136 | 5283 | 5371 |
| SURPLUS (+) / SHORTAGE (-) | 469 | 869 | 469 | 116 | 454 | 436 | 686 | 236 | -17 | 271 |
| JUNE 2012 |  |  |  |  |  |  |  |  |  |  |
| DEMAND | 4700 | 4200 | 4800 | 5300 | 5200 | 4850 | 4600 | 5100 | 5500 | 5200 |
| AVAILABILITY | 5259 | 5234 | 5359 | 5594 | 5574 | 5325 | 5325 | 5450 | 5685 | 5665 |
| SURPLUS (+) / SHORTAGE (-) | 559 | 1034 | 559 | 294 | 374 | 475 | 725 | 350 | 185 | 465 |
| JULY 2012 |  |  |  |  |  |  |  |  |  |  |
| DEMAND | 4600 | 4300 | 4750 | 5200 | 5000 | 4500 | 4200 | 4700 | 5200 | 5000 |
| AVAILABILITY | 5584 | 5559 | 5559 | 5794 | 5824 | 5576 | 5551 | 5551 | 5786 | 5816 |
| SURPLUS (+) / SHORTAGE (-) | 984 | 1259 | 809 | 594 | 824 | 1076 | 1351 | 851 | 586 | 816 |
| AUG 2012 |  |  |  |  |  |  |  |  |  |  |
| DEMAND | 4700 | 4200 | 4800 | 5500 | 5300 | 4300 | 3800 | 4600 | 4900 | 4800 |
| AVAILABILITY | 5246 | 5221 | 5221 | 5456 | 5486 | 5159 | 5134 | 5134 | 5369 | 5399 |
| SURPLUS (+) / SHORTAGE (-) | 546 | 1021 | 421 | -44 | 186 | 859 | 1334 | 534 | 469 | 599 |
| SEP 2012 |  |  |  |  |  |  |  |  |  |  |
| DEMAND | 4500 | 4200 | 4500 | 4900 | 4800 | 4100 | 3600 | 4300 | 4300 | 4200 |
| AVAILABILITY | 4869 | 4869 | 4869 | 5016 | 5104 | 4869 | 4869 | 4869 | 5016 | 5104 |
| SURPLUS (+) / SHORTAGE (-) | 368 | 668 | 369 | 116 | 304 | 768 | 1269 | 569 | 716 | 904 |

Power supply position for the period October 2012 to March 2013 is as under :-

All Figures in MW

| MONTH | 1st Fortnight | 2nd fortnight |
| --- | --- | --- |
| OCTOBER 2012 | 00-10 | 10-18 | 18-22 | 22-24 |  | 00-10 | 10-18 | 18-22 | 22-24 |  |
| DEMAND | 3600 | 3850 | 4000 | 3600 |  | 3300 | 3500 | 3800 | 3450 |  |
| AVAILABILITY | 4045 | 4167 | 4320 | 4167 |  | 4045 | 4167 | 4320 | 4167 |  |
| SURPLUS (+) / SHORTAGE (-) | 445 | 317 | 319 | 567 |  | 745 | 667 | 519 | 717 |  |

| MONTH | 1st Fortnight | 2nd fortnight |
| --- | --- | --- |
| NOVEMBER 2012 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 |
| DEMAND | 2450 | 3000 | 3400 | 3400 | 2700 | 2300 | 3000 | 3300 | 3200 | 2500 |
| AVAILABILITY | 4261 | 4719 | 4444 | 4719 | 4261 | 4261 | 4719 | 4444 | 4719 | 4261 |
| SURPLUS (+) / SHORTAGE (-) | 1811 | 1719 | 1044 | 1319 | 1561 | 1961 | 1719 | 1144 | 1519 | 1761 |
| DECEMBER 2012 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 |
| DEMAND | 2300 | 3200 | 3300 | 3300 | 2600 | 2300 | 4000 | 3700 | 3500 | 3400 |
| AVAILABILITY | 4303 | 4761 | 4486 | 4761 | 4303 | 4303 | 4761 | 4486 | 4761 | 4303 |
| SURPLUS (+) / SHORTAGE (-) | 2003 | 1561 | 1186 | 1461 | 1703 | 2003 | 761 | 786 | 1261 | 903 |
| JANUARY 2013 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 |
| DEMAND | 2400 | 4200 | 3700 | 3700 | 3100 | 2500 | 4000 | 3600 | 3600 | 3000 |
| AVAILABILITY | 4293 | 4751 | 4476 | 4751 | 4293 | 4293 | 4751 | 4476 | 4751 | 4293 |
| SURPLUS (+) / SHORTAGE (-) | 1893 | 551 | 776 | 1051 | 1193 | 1793 | 751 | 876 | 1151 | 1293 |
| FEBRUARY 2013 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 | 00-06 | 06-12 | 12-18 | 18-22 | 22-24 |
| DEMAND | 2400 | 3700 | 3400 | 3500 | 3000 | 2200 | 3500 | 3200 | 3400 | 2700 |
| AVAILABILITY | 4086 | 4544 | 4269 | 4544 | 4086 | 4086 | 4544 | 4269 | 4544 | 4086 |
| SURPLUS (+) / SHORTAGE (-) | 1686 | 844 | 869 | 1044 | 1086 | 1886 | 1044 | 1069 | 1144 | 1386 |
| MARCH 2013 | 00-10 | 10-18 | 18-22 | 22-24 |  | 00-10 | 10-18 | 18-22 | 22-24 |  |
| DEMAND | 3400 | 3500 | 3200 | 2500 |  | 3200 | 3300 | 3400 | 3000 |  |
| AVAILABILITY | 4229 | 4351 | 4504 | 4351 |  | 4279 | 4401 | 4554 | 4401 |  |
| SURPLUS (+) / SHORTAGE (-) | 829 | 851 | 1304 | 1851 |  | 1079 | 1101 | 1154 | 1401 |  |

Assumptions

i)	Availability from Un-allocated quota of Central Sector has been considered as NIL.

ii)	COD of Jhajjar Unit-II (500MW) is declared on 21.04.2012 and DPPG has recommended the surrender of one unit of Jhajjar for the period 01.04.12 to 30.06.12 and Govt. of India has allocated allocation of power from Jhajjar Unit-1 upto 31.05.12 to Andhra Pradesh and Kerala.  As such, one unit of Jhajjar has been considered for May 2012 and both units are considered from June 2012 onwards.

iii)	Availability from DVC has been considered as 375 MW.

iv)	Availability from Hydro stations has been considered as 50% during the day time, 75% during evening peak and 30% during the rest of the period in the month of April 2012. During May & Sept.2012 - 75%, 90% and 50% during day time, evening peak and rest of the time respectively.  During the month of June-Aug 2012 during the day time 90%, evening peak 95% and rest of the time 50% from Hydro sources.

v)	Dadri(Th) Unit-2 (210MW) is scheduled for Annual Maintenance / Boiler Overhauling for the period 23.08.2012 to 26.09.2012

vi)	BTPS Unit-2 (95MW) is planned for maintenance from 01.08.2012 to 20.08.2012 and Unit-5 (210MW) from 01.09.2012 to 10.10.2012 for Annual Over-hauling.

vii)	One GT of Pragati would remain under shut-down (150MW effective capacity) for carrying out mandatory maintenance work.

viii)	Availability from Hydro stations has been considered as 0% during Night hours (00.00hrs. to 06.00hrs), 75% during Morning and Evening Peak Hours and 30% during rest of the period for November 2012 to February 2013.

ix)	Availability from Hydro Stations has been considered as 30% during Morning Hours (0- 10hrs), 50% during Day time (10.00-18.00hrs), 75% during Evening Peak Hours (18.00-22.00hrs) and 50% during rest of the period (22.00hrs.-24.00hrs) for Oct.12 & March 2013.

x)	One 95MW unit at BTPS is planned for maintenance for the during October 2012

xi)	Dadri (Th)-II Unit-2 (490MW capacity) is planned for maintenance during Oct. 2012

xii)	One unit of Jhajjar is out during the period February 2013 and March 2013 for maintenance.

xiii)	200MW return of banking power each by BRPL and BYPL has been considered during October 2012 to March 2013.

It was also informed that considering the above power supply position, Delhi Power Procurement Group (DPPG) in its meeting held on 26.04.2012 has identified clear cut surpluses from May 2012 to March 2013 as under :

Monthwise surplus power for Summer season

All figures in MW

|  | Duration : 03.00hrs. To 09.00hrs. |  |  |
| --- | --- | --- | --- |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| May-12 | 271 | 249 | 247 | 80 | 21 | 869 |
| Jun-12 | 233 | 359 | 316 | 104 | 21 | 1034 |
| Jul-12 | 566 | 281 | 287 | 104 | 21 | 1259 |
| Aug-12 | 425 | 256 | 266 | 58 | 16 | 1021 |
| Sep-12 | 171 | 185 | 230 | 73 | 9 | 669 |
|  | Duration : 09.00hrs. - 12.00hrs. |  |  |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| May-12 | 128 | 145 | 151 | 25 | 19 | 469 |
| Jun-12 | 128 | 198 | 162 | 50 | 19 | 559 |
| Jul-12 | 414 | 169 | 185 | 20 | 19 | 809 |
| Aug-12 | 197 | 99 | 113 | -3 | 14 | 421 |
| Sep-12 | 76 | 112 | 167 | 7 | 7 | 369 |
|  | Duration : 12.00hrs. - 18.00hrs. |  |  |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| May-12 | -53 | 33 | 28 | -40 | 14 | -17 |
| Jun-12 | 61 | 99 | 56 | -45 | 14 | 185 |
| Jul-12 | 348 | 133 | 146 | -55 | 14 | 586 |
| Aug-12 | 256 | 135 | 153 | -90 | 14 | 469 |
| Sep-12 | 260 | 227 | 290 | -63 | 2 | 716 |

|  | Duration : 18.00hrs. - 24.00hrs. |  |  |
| --- | --- | --- | --- |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| May-12 | 33 | 104 | 86 | 34 | 14 | 271 |
| Jun-12 | 113 | 180 | 124 | 34 | 14 | 465 |
| Jul-12 | 411 | 189 | 188 | 14 | 14 | 816 |
| Aug-12 | 273 | 160 | 165 | -19 | 19 | 599 |
| Sep-12 | 301 | 266 | 317 | 13 | 7 | 904 |

Note :	(-)ve indicates shortages.

Month wise surplus of Winter-2012-13

|  | Duration : 00.00hrs. To 06.00hrs. |  |
| --- | --- | --- |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| Oct 2012 | 128 | 131 | 435 | 43 | 9 | 745 |
| Nov 2012 | 591 | 422 | 745 | 185 | 19 | 1961 |
| Dec 2012 | 616 | 437 | 761 | 175 | 14 | 2003 |
| Jan 2013 | 537 | 388 | 709 | 145 | 14 | 1793 |
| Feb 2013 | 567 | 407 | 728 | 165 | 19 | 1886 |
| Mar 2013 | 252 | 210 | 518 | 85 | 14 | 1079 |
|  | Duration : 06.00hrs. - 12.00hrs. |  |  |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| Oct 2012 | 128 | 131 | 435 | 43 | 9 | 745 |
| Nov 2012 | 527 | 382 | 701 | 95 | 14 | 1719 |
| Dec 2012 | 124 | 130 | 432 | 65 | 9 | 761 |
| Jan 2013 | 127 | 131 | 434 | 55 | 4 | 751 |
| Feb 2013 | 228 | 195 | 502 | 105 | 14 | 1044 |
| Mar 2013 | 275 | 224 | 533 | 60 | 9 | 1101 |
|  | Duration : 12.00hrs. - 18.00hrs. |  |  |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| Oct 2012 | 105 | 117 | 419 | 23 | 4 | 667 |
| Nov 2012 | 278 | 210 | 535 | 111 | 9 | 1144 |
| Dec 2012 | 127 | 115 | 434 | 101 | 9 | 786 |
| Jan 2013 | 177 | 147 | 467 | 71 | 14 | 876 |
| Feb 2013 | 241 | 187 | 510 | 121 | 9 | 1069 |
| Mar 2013 | 280 | 211 | 537 | 111 | 14 | 1154 |
|  | Duration : 18.00hrs. - 22.00hrs. |  |  |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| Oct 2012 | 17 | 46 | 360 | 88 | 9 | 520 |
| Nov 2012 | 435 | 308 | 640 | 121 | 14 | 1519 |
| Dec 2012 | 325 | 239 | 566 | 121 | 9 | 1261 |
| Jan 2013 | 286 | 215 | 540 | 101 | 9 | 1151 |
| Feb 2013 | 267 | 203 | 528 | 131 | 14 | 1144 |
| Mar 2013 | 373 | 269 | 599 | 151 | 9 | 1401 |
|  | Duration : 22.00hrs. - 24.00hrs. |  |  |
| Month | BRPL | BYPL | NDPL | NDMC | MES | Total |
| Oct 2012 | 83 | 87 | 405 | 138 | 4 | 717 |
| Nov 2012 | 517 | 375 | 695 | 165 | 9 | 1761 |
| Dec 2012 | 145 | 143 | 446 | 155 | 14 | 903 |
| Jan 2013 | 333 | 260 | 571 | 115 | 14 | 1293 |
| Feb 2013 | 362 | 279 | 591 | 145 | 9 | 1386 |
| Mar 2013 | 373 | 269 | 599 | 151 | 9 | 1401 |

From the above position, it is very clear that Delhi is having substantial surplus power.  Delhi Power Procurement Group has already requested the State Government to request the Central Government to reallocate the entire share of Delhi from Aravali Jhajjar units till 31.03.2013.  The present allocation of 23% of capacity (out of 1000MW Capacity) is reallocated to Kerala and Andhra Pradesh only upto 31.05.2012.

It was also informed that SLDC has already given a report to DERC regarding surplus power as advised in the meeting held at DERC on 13.04.2012.  SLDC has proposed the Commission regarding the disposal of surplus power by way of reallocation of allocation of Delhi from various sources as under :

| S. N. | Name of the unit from where surrender was made | MW capacity surrendered | %age share of Delhi proposed to be surrendered | Period of surrender | duration of surrender | Approximate rate |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Jhajjar | 462 | 100 (for unit-I & II) | 01.05.2012 to 31.03.12 | 00.00-24.00hrs. | Fixed Charges :Rs. 1.80/unit Variable Charges: Rs.3.50/Unit Total :Rs.5.30/unit |
| 2 | Dadri Thermal Stage-II | 735 | 100 | Nov.2012 | 00.00-06.00hrs. | Fixed Charges :Rs. 1.25/unit Variable Charges: Rs.2.65/Unit Total :Rs.3.90/unit |
|  |  | 300 | 40 |  | 06.00-24.00hrs. |  |
|  |  | 735 | 100 | Dec.2012 | 00.00-06.00hrs. 22.00-24.00hrs. |  |
|  |  | 300 | 40 |  | 06.00-22.00hrs. |  |
|  |  | 735 | 100 | Jan.2013 | 00.00-06.00hrs. |  |
|  |  | 300 | 40 |  | 12.00.-24.00hrs. |  |
|  |  | 735 | 100 | Feb.2013 | 00.00-06.00hrs. |  |
|  |  | 300 | 40 |  | 12.00.-24.00hrs. |  |
|  |  | 735 | 100 | Mar.2013 | 00.00-06.00hrs. |  |
|  |  | 735 | 100 |  | 22.00.-24.00hrs. |  |
| 3 | Farakka | 22 | 100 | 01.11.12 to 31.03.13 | 00.00-24.00hrs. | Farakka Fixed Charges :Rs. 0.80/unit Variable Charges : Rs.3.50/Unit Total :Rs.4.30/unit Kahalgaon-I Fixed Charges :Rs. 0.85/unit Variable Charges : Rs.2.90/Unit Total :Rs.3.75/unit Kahalgaon-II Fixed Charges :Rs. 1.10/unit Variable Charges : Rs.2.90/Unit Total :Rs.4.00/unit |
| 4 | Kehalgaon-I | 51 | 100 |  |  |  |
| 5 | Kahalgaon-II | 157 | 100 |  |  |  |
| 6 | Dadri Thermal Stage-I | 200 | 26 | Nov 12 to March 2013 | 00.00-06.00hrs 22.00-24.00hrs. | Fixed Charges :Rs.0.83/unit Variable Charges : Rs.3.00/Unit Total :Rs.3.83/unit |

The surrender of Central Sector Generating Stations is having higher priority in corridor allocation, if the same is done well in advance.  In the tariff regulations of CERC notified on 19.01.2009 applicable for the period 01.04.2009 to 31.03.2014, the Regulation 32(2) Note-2 stipulates the methodology of surrender.  For clarity, the same is reproduced hereunder :

Note 2

The beneficiaries may propose surrendering part of their allocated firm share to other States within / outside the region. In such cases, depending upon the technical feasibility of power transfer and specific agreements reached by the generating company with other States within/ outside the region for such transfers, the shares of the beneficiaries may

be prospectively re-allocated by the Central Government for a specific period (in complete months) from the beginning of a calendar month. When such re-allocations are made, the beneficiaries who surrender the share shall not be liable to pay capacity charges for the surrendered share. The capacity charges for the capacity surrendered and reallocated as above shall be paid by the State(s) to whom the surrendered capacity is allocated. Except for the period of reallocation of capacity as above, the beneficiaries of the generating

station shall continue to pay the full capacity charges as per allocated capacity shares.

Any such reallocation and its reversion shall be communicated to all concerned by the Member Secretary, Regional Power Committee in advance, at least three days prior to such reallocation or reversion taking effect.

In case, no takers are available for the surrendered power, the left over option is disposing the surplus in day ahead markets, UI mechanism on real time basis based on the system conditions and permissible limits and lastly backing down the costly sources upto the technical bare minimum limits.

Considering the surplus power position, representatives of all Distribution companies expressed their distress in booking of allocation of Aravali Power Jhajjar units to Delhi in spite of requisitioning NIL requirement from the Station.  They requested representative of Aravali Power to give the reasons of high cost of generation and measures taken by the Generating Company to reduce the cost by way of low cost coal etc.  They also requested to highlight the Aravali Power Company’s endeavour to reallocate the allocation of share of Delhi State to needy States as Delhi Distribution Companies have already intimated that they would not require any power from the station upto 31.03.2013.

The representative of Aravali Power Company mentioned that the fixed charges of the Station has been reduced to Rs. 1.80/unit with the commissioning of 2nd unit of the Station. (the provisional fixed charges as fixed by CERC is Rs. 1.63/unit).  With the commissioning of the 3rd unit, it would further be reduced.  With regard to variable charges, the charges are higher because of non availability of indigenous coal to the extent required to operate the units.  To maintain stability of generation, imported coal is also being used. He further informed that the fuel supply agreement is in the stage of finalization with Coal India Ltd.  He hoped that after the execution of Fuel Agreement and improvement in indigenous coal supply, the rate of the station would be reduced.

As far as the scheduling of power from Jhajjar to Delhi Utilities, he informed that the scheduling responsibility lies with NRLDC which schedules power as per the requirement and for ensuring the operation of the units to the extent of technical minimum requirement of generation to run the station.  As such, it appears that the power is being scheduled to Delhi Utilities at the time when the overall requirement of beneficiaries is less than 70% of ex-bus generation which is the technical minimum limit to run the units.  With regard to reallocation of power is concerned, it is the within the purview of the Ministry of Power, Govt. of India on the basis of the request of the State Government.

He further requested the Delhi utilities to schedule power from the station as the asset is built for the benefit of Delhi.

Impact of surrender of surplus power during last Winter.

SLDC presented the details of surrender of surplus power by way of reallocation of various sources as under :-

| S.N. | Name of the unit from where surrender was made | MW capacity surrendered | Duration of surrender | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Jhajjar | 231 | 07.10.11 to 31.05.12 | 100% share of Delhi from unit-1 upto 20.04.2012 and 50% share from 21.04.2012 on round the clock basis to Andhra Pradesh and Kerala. |
| 2 | Dadri Thermal Stage-II | 735 | 08.01.12 to 01.02.12 | Though the allocation made upto 29.02.2012 (00.00-06.00hrs), due to corridor constraints, Hon’ble High Court of Andhra Pradesh quashed the allocation from 02.02.2012 to pave way to honour earlier contracts through the corridors. |
| 3 | Farakka | 22 | 01.02.12 to 29.02.12 | 100% share of Delhi surrendered and reallocated to West Bengal during 00.00hrs. to 24.00hrs. |
| 4 | Kehalgaon-I | 51 |  | 100% share of Delhi surrendered and reallocated to West Bengal during 00.00hrs. to 06.00hrs. |
| 5 | Kahalgaon-II | 157 |  | 100% share of Delhi surrendered and reallocated to West Bengal during 00.00hrs. to 06.00hrs. |

Due to the surrender of above power allocation from various sources, Delhi could save approximately Rs. 225 Crores as detailed hereunder:-

| Station | Month | Net saving in Rs Crores |
| --- | --- | --- |
| Jhajjar | Oct.11 | 15 |
|  | Nov.11 | 27 |
|  | Dec.11 | 26 |
|  | Jan.12 | 40 |
|  | Feb.12 | 39 |
|  | Mar.12 | 40 |
| Dadri Thermal-II | Jan.12 | 22 |
|  | Feb.12 | 1 |
| Farakka | Feb.12 | 2 |
| Kahalgaon-I | Feb.12 | 4 |
| Kahalgaon-II | Feb.12 | 23 |
| Total |  | 238 |

Note:	The above saving is computed considering the allocation to Delhi in scenario of non allocation to other States and return through UI transactions for under drawal considering the mandatory technical minimum off take for the same.

Further, already the cash strapped Discoms could shelve the responsibility of immediate payment liability to the tune of Rs. 405Crores under:-

| Station | Month | Energy surrendered in Mus | Rate in Ps/Unit | Payment liability in Rs. Crores |
| --- | --- | --- | --- | --- |
| Jhajjar | Oct.11 | 87 | 573 | 50 |
|  | Nov.1 | 109 | 573 | 62 |
|  | Dec.11 | 112 | 573 | 64 |
|  | Jan.12 | 112 | 573 | 64 |
|  | Feb.12 | 105 | 573 | 60 |
|  | Mar.12 | 112 | 573 | 64 |
|  | Total | 639 | 573 | 366 |
| Dadri Thermal-II | Jan.12 | 69 | 394 | 27 |
|  | Feb.12 | 3 | 394 | 1 |
|  | Total | 72 | 394 | 28 |
| Farakka | Feb.12 | 4 | 446 | 2 |
| Kahalgaon-I | Feb.12 | 8 | 371 | 3 |
| Kahalgaon-II | Feb.12 | 13 | 391 | 5 |
| Total |  | 737 | 549 Weighted Avg. | 405 |

It is also pertinent that due to non payment of UI amount by some States, Delhi Utilities have to get Rs. 350 Crores from Regional UI Pool Account.

Due to corridor constraints, such type of transfer may not be sustained during the next winter as the major takers of the power are Southern Regional Utilities during winter season.  As per the indications available, the integration of Southern Regional Grid with rest of the Grid (NEW Grid) can be possible only after March 2014.  After the integration only, more power transfer could be possible to Southern Region Grid.

10	CAPACITOR INSTALLATION PLAN

Utility wise installed capacity of capacitors as on 31.03.2012 is as under :-

All figures in MVAR

| Utility | Installed capacity | Working capacity as on date | Additional capacity planned for this summer | LT Capacitors | Remarks |
| --- | --- | --- | --- | --- | --- |
| IPGCL | 20 | 10 | -- | -- |  |
| DTL | 754 | 694 | -- | -- |  |
| BYPL | 851 | 824 | 89.79 | 109 | Out of 89.79MVAR HT Capacitors, only 29.31MVAR have been approved by DERC, 60.48MVAR is under approval. |
| BRPL | 1185 | 1146 | 186.3 | 241 | 30.24MVAR (20.16MVAR at Vasant Kunj D Block and 10.08MVAR at DC Saket) dismantled by BRPL for paving the bays for 66kV and 33kV feeders to be energized before CWG 2010. |
| TPDDL | 719 | 719 | 21.76 | 119 | 21.76MVAR HT capacitors approved by DERC. |
| NDMC | 111 | 106 | 75 | 25 | HT Capacitors are likely to be commissioned by end of July 2012. |
| MES | 21 | 21 | -- | -- |  |
| Total | 3662 | 3520 | 372.85 | 494 |  |

As per the Capacitor Study conducted by NRPC, the required installed capacity of the capacitors in Delhi system is as under :-

All figures in MVAR

| Capacity as on 31.03.2009 | Additional required for 2009-10 | Addition required for 2010-11 | Addition required for 11-12 | Addition required for 2012-13 |
| --- | --- | --- | --- | --- |
| 3476 | 0 | 567 | 367 | 184 |
| Capacity required as on 31.03.2011 | 4043 |
| Capacity required as on 31.03.2012 | 4410 |
| Installed capacity as on 31.03.2013 | 4594 |
| Installed capacity as on 31.03.2012 on HT level | 3662 |
| Additional capacity requirement on HT level by 31.03.2013 | 932 |

The capacity installation programme is continuously being monitored by NRPC at forum like OCC, TCC and NRPC level.  Likewise in Delhi, the same is monitored by Delhi OCC on monthly meetings.

Delhi Discoms informed in these fora that the capacity addition in slow pace due to delay in getting clearance by them from DERC.  DERC has given the direction to Discoms to plan the capacitors near loads i.e. at LT level.  The capacitors installed at LT level are not considered as capacity addition by NRPC.

Further, DTL being STU has been advised by Delhi OCC to carry out the study, if required through CPRI for assessing actual requirement of Capacitors and finalizing the locations.  Even after lapsing considerable time, Delhi OCC could not get the status of such studies.

It was informed that the Capacitor Installation Programme was discussed in the meeting taken by Joint Secretary (O&M), Govt. of India on 18.04.2012 for reviewing power supply position and preparedness during the summer 2012 in Delhi.  It was advised for the installation of adequate capacitors as per the assessment of NRPC for voltage support for meeting the increased demand during summer months.

SLDC presented the reactive power drawal by Delhi from the Grid during the year 2007-08 to 2012-13 as under :-

| Year | Reactive energy drawal in Million Units | Amount in Rs. Lacs | Net Amount in Rs. Lacs |
| --- | --- | --- | --- |
|  | High voltage | Low Voltage | High voltage | Low Voltage |  |
| 2007-08 | 349 | 9 | -104 | 3.66107 | -100.63568 |
| 2008-09 | 265 | -2 | -146 | -1.19435 | -145.88434 |
| 2009-10 | 6 | 234 | -3 | 134.37336 | 130.91876 |
| 2010-11 | 106 | 285 | -104 | 284.05988 | 180.04506 |
| 2011-12 | 270 | -4 | -284 | -3.95262 | -287.97363 |
| Total | 997 | 522 | -642 | 416.94734 | -223.52983 |

Note :-  In case of energy, (-)ve indicates injection and in case of amount (-)ve indicates

receivable.

The above data reveal that probably due to addition of cables etc, the voltage profile in Delhi has improved substantially.  However, a substantial amount of reactive power drawal is occurring though the penalty is not being imposed due to drawal in high voltage.  For example, at the time of peak demand, the total drawal by all Distribution Companies was of the order of 538MVAR though the voltages at the exchange points were within the normal range stipulated in Indian Electricity Grid Code, 400kV voltages were low which is evident from the following table :-

STATEMENT SHOWING SUBSTATION-WISE TRANSFORMER  LOADING (CONNECTED LOAD) AT THE TIME OF OCCURRENCE OF MAX DEMAND (5028MW) IN DELHI SYSTEM

| SL NO | NAME OF THE GRID | 220/66 & 220/33 KV , 100 MVA POWER TRANSFORMER | 02.08.2011 AT 15:07:47HRS LOAD 5028 MW | VOLTAGE |
| --- | --- | --- | --- | --- |
|  |  | INSTALLED CAPACITY (MVA) | INSTALLED CAPACITY (MW) p.f. 0.95 at Transmission Level |  |  |
|  | NORTH DELHI | MW | MVAR | 220kV | 66kV | 33kV | 11kV |
| 1 | Narela | 300 | 240 | 197 | -26 | 211 | 64 | -- | 10.9 |
| 2 | Gopalpur | 300 | 240 | 206 | 18 | 206 | 63 | 30.5 | 9.8 |
| 3 | Rohini | 400 | 320 | 336 | -11 | 208 | 62 | -- | 11 |
| 4 | Shalimarbagh | 300 | 240 | 202 | 45 | 207 | -- | 31.2 | 9.9 |
| 5 | Bawana | 100 | 80 | 63 | 23 | 211 | 59.7 | -- | -- |
| 6 | Kanjhawala | 200 | 160 | 69 | 35 | 210 | 63.3 | -- | 10.4 |
| 7 | Through Rohtak Road grid of BBMB | 400 | 320 | 195 | 61 |  |  |  |  |
|  | TOTAL | 2000 | 1600 | 1268 | 145 |  |  |  |  |
| WEST DELHI |  |  |  |  |  |
| 1 | Najafgarh | 400 | 320 | 345 | 5 | 210 | 62 | -- | 11 |
| 2 | Papankalan-1 | 400 | 320 | 317 | 27 | 211 | 60 | -- | 10 |
| 3 | Papankalan-2 | 200 | 160 | 132 | 35 | 210 | 62 | -- |  |
| 4 | Naraina | 300 | 240 | 120 | 0 | 209 | -- | 30.5 | 11 |
|  | TOTAL | 1300 | 1040 | 914 | 67 |  |  |  |  |
| SOUTH DELHI & NDMC |  |  |  |  |  |
| 1 | Mehrauli | 300 | 240 | 222 | 42 | 212 | 64 | -- | 9.6 |
| 2 | Okhla | 500 | 400 | 366 | 0 | 207 | 63 | 31.5 | 10.3 |
| 3 | Sarita Vihar | 200 | 160 | 149 | 15 | 208 | 63 | -- | 10.6 |
| 4 | Lodhi Road | 200 | 160 | 166 | 59 | 218 | -- | 32.8 | 10.6 |
| 5 | Vasant Kunj | 360 | 288 | 140 | 0 | 205 | 61 | -- | 10.3 |
| 6 | Ridge Valley | 320 | 256 | 67 | 17 | 211 | -- | -- | -- |
| 7 | DIAL | 320 | 256 | 24 | 1 | 212 | 62.2 | -- | -- |
| 8 | Masjid Moth | 200 | 160 | 58 | 10 | 218 | -- | 31.5 | -- |
|  | TOTAL | 2400 | 1920 | 1192 | 144 |  |  |  |  |
| EAST DELHI |  |  |  |  |  |
| 1 | Wazirabad | 300 | 240 | 241 | 46 | 205 | 60 | -- | 9.9 |
| 2 | Patparganj | 550 | 440 | 252 | 0 | 210 | 66 | 31 | 10.5 |
| 3 | Geeta colony | 200 | 160 | 80 | 31 | 204 | -- | 29 | -- |
| 4 | Gazipur | 200 | 160 | 140 | 0 | 210 | 62 | -- | 10.6 |
|  | TOTAL | 1250 | 1000 | 713 | 77 |  |  |  |  |

| SL NO | NAME OF THE GRID | 220/66 & 220/33 KV , 100 MVA POWER TRANSFORMER | 02.08.2011 AT 15:07:47HRS LOAD 5028 MW | VOLTAGE |
| --- | --- | --- | --- | --- |
|  |  | INSTALLED CAPACITY (MVA) | INSTALLED CAPACITY (MW) p.f. 0.95 at Transmission Level |  |  |
|  | CENTRAL DELHI & NDMC | MW | MVAR | 220kV | 66kV | 33kV | 11kV |
| 1 | Parkstreet | 400 | 320 | 241 | 27 | 218 | 62.2 | 32 | -- |
| 2 | IP Extension (GT) | 260 | 208 | 123 | -1 | 216 | -- | -- | -- |
| 3 | Subzimandi | 200 | 160 | 109 | 7 | 204 | -- | 30.5 | 9.5 |
| 4 | Kashmeregate | 200 | 160 | 96 | 20 | 207 | -- | 31.5 | 10.5 |
| 5 | IP Station | 300 | 240 | 209 | 46 | 215 | -- | 32 | -- |
| 6 | Rajghat | 175 | 140 | 112 | 6 | 218 | -- | 31 | -- |
|  | TOTAL | 1535 | 1228 | 890 | 105 |  |  |  |  |
|  | Total |  |  |  | 538 |  |  |  |  |
|  | Voltage of 400kV S/Stns around Delhi at 15.07hrs. on 02.08.2012 |  |  |
|  |  |  | IN KV |  |  |  |  |  |  |
|  | MANDOLA VOLTAGE | 391 |  |  |  |  |  |  |
|  | BAWANA |  | 379 |  |  |  |  |  |  |
|  | BAMNAULI |  | 385 |  |  |  |  |  |  |
|  | MAHARANI BAGH | 383 |  |  |  |  |  |  |
|  | MUNDKA |  | 386 |  |  |  |  |  |  |

In such scenario, the detailed study should be conducted for arriving actual requirement of capacitors and the locations where they should be installed.  The operation of the capacitors is also required to closely monitored to avoid drawal of reactive power under low voltage conditions and injection during high voltage conditions.

All Distribution Licensees requested SLDC to provide the real time data of reactive power drawal in each feeders so that corrective action can be taken by the concerned.  SLDC expressed its inability in the present data telemetry structure but the same could be achieved after the integration of Discom’s data in the proposed ULDC Phase-II Scheme.

TPDDL representative enquired about the reactive charges accumulated at Regional level and State level.

It was informed that at Regional level, virtually no amount is coming as reactive charges though a substantial amount is due to Delhi as exhibited above.  As far as, Intra State Reactive Energy charges are concerned, the same is being maintained by DTL.

BYPL representative mentioned that as per the tariff order of DERC in respect of Transmission Tariff of DTL, it has been categorically stated that the reactive charges being collected from Distribution Licensees should be kept in a separate account.  He quoted the relevant portions of the order dated 20.12.2007 and 26.08.2011 as under :-

Quote from ARR order of DTL dated 20.12.2007:-

Reactive Energy

6.8	The Commission directs the petitioner to maintain a separate account for the reactive energy wheeled and the respective reactive charges levied to the Discoms.  Since no proposal for reactive energy charges was included by the petitioner in this petition, the existing arrangement for leavy of reactive energy charges shall continue.  The Petitioner is directed to fill an appropriate petition for reactive energy charges within three months of issue of this order.

Quote from ARR order of DTL dated 26.08.2011:-

5.14	The Commission directs the DTL to maintain a separate account for the reactive energy wheeled and the respective reactive charges levied to the Discoms.

BYPL representative was of the view that DTL should transfer the reactive energy charges collected from Distribution Licensees to the Reactive Energy Charges Account being maintained by SLDC.  He also intended to know the total charged accumulated in this regard from 2007-08 to 2011-12.  SLDC representative informed the details as per the information available with SLDC as under :-

| Year | Details | NDPL | BRPL | BYPL | NDMC | MES | Total | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2007-09 | Reactive Drawal in Mus | 1154 | 891 | 553 | 905 | 134 | 3637 | Rate 2Ps per kVARh for the entire drawal of the reactive energy irrespective of voltge |
|  | Amount in Rs. Lacs | 231 | 178 | 111 | 181 | 27 | 727 |  |
| 2009-10 | Reactive Drawal in Mus | 541 | 798 | 435 | 346 | 62 | 2182 |  |
|  | Amount in Rs. Lacs | 108 | 160 | 87 | 69 | 12 | 436 |  |

| Name of Discoms | Year | Reactive energy Drawal in Mus | Amount in Rs. Lacs | Net Amount in Rs. Lacs | Remarks |
| --- | --- | --- | --- | --- | --- |
|  |  | High Voltage | Low Voltage | High Voltage | Low Voltage |  |  |
| NDPL | 2010-11 | -25 | 29 | 26 | 27 | 53 | Rate April 2010 : 6Ps/kVARh May 10 to Mar.11 : 10Ps/kVARh 2011-12 : 10.5Ps/kVARh The charges are applicable for drawal / injection for transaction above 103% and below 97% of the rated voltage at exchange points. No charges are applicable for reactive power exchange for the voltage profile between 97% to 103% of the rated voltage at exchange points. |
|  | 2011-12 | 3 | 64 | -3 | 68 | 65 |  |
|  | Total | -23 | 94 | 23 | 95 | 118 |  |
| BRPL | 2010-11 | -18 | 275 | 14 | 261 | 275 |  |
|  | 2011-12 | -1 | 286 | 1 | 300 | 301 |  |
|  | Total | -19 | 561 | 16 | 561 | 576 |  |
| BYPL | 2010-11 | 17 | 101 | -17 | 93 | 76 |  |
|  | 2011-12 | 34 | 42 | -36 | 44 | 8 |  |
|  | Total | 51 | 143 | -53 | 137 | 84 |  |
| NDMC | 2010-11 | 68 | 110 | -66 | 104 | 38 |  |
|  | 2011-12 | 91 | 56 | -95 | 59 | -37 |  |
|  | Total | 159 | 165 | -161 | 162 | 1 |  |
| MES | 2010-11 | 4 | 22 | -4 | 21 | 17 |  |
|  | 2011-12 | 4 | 13 | -4 | 14 | 10 |  |
|  | Total | 8 | 35 | -8 | 35 | 27 |  |
| Total Discoms | 2010-11 | 46 | 537 | -47 | 506 | 459 |  |
|  | 2011-12 | 130 | 461 | -137 | 484 | 347 |  |
|  | Total | 176 | 998 | -183 | 990 | 807 |  |

From the above, it has been observed that as on 31.03.2012, the total reactive power charges collected by Delhi Transco Ltd from Discoms is about Rs. 19 Crores. The representatives of Distribution Licensees were of the view that these amount accumulated should be utilized for system improvement for example for installing adequate capacitors at the required locations in the same line of methodology adopted at Regional level.

Concluding the discussions, GCC decided the following :-

- Delhi Operation Coordination Committee may discuss in details the capacitors installation programme and the requirement of capacitors based on the study to be conducted by a reputed agency like CPRI to find the realistic requirement of capacitors and their locations.

- Delhi Commercial Sub-Committee may draw out the methodology of optimum use of fund accumulated in Reactive Pool Account being maintained by DTL for voltage improvement.

- After getting the details, GCC may take a view for recommending the optimum utilization of the funds available in the Reactive Pool Account being maintained by DTL to DERC for decision.

11	TRIPPING OF 220/66KV 160MVA TXS. INSTLLED AT PRAGATI SUB-STATION (EARLIER KNOWN AS IP EXT.)

Two 220/66kV 160MVA Txs are installed at 220kV Pragati Grid S/Stn (earlier known as IP Ext. S/Stn) of DTL.  These transformers establish link of IPGCL’s GT Power Station (270MW capacity) with the Grid.  After meeting the radial load at 66kV level namely (a) 66kV Vidyut Bhawan Ckt-I & II (b) 66kV School Lane Ckt-I & II (c) 66kV DMRC Ckt-I & II (d) 66kV Akshardham Ckt. the balance generation of the station is fed to the Grid through these transformers.  Of late, it has been observed that these transformers trip due to faults even at in remote ends causing islanding of GT Station from the Grid and most of the collapsing affecting VVIP and other important areas.

In the agenda, it has been mentioned that 160MVA Tx-1 tripped 29 times upto 04.03.2012 from the date of the installation of the transformer i.e 29.12.2008 and the second transformer tripped 14 times from 18.09.2010 (the date of the installation of the transformer) upto 04.03.2012 (these transformers are replacement of earlier 220/66kV 100MVA Txs).

The tripping of both transformers resulting the islanding of GT Station from the Grid and many time causing the tripping of all running GTs and thereby affecting the VVIP load and DMRC network. The recent one occurred on 04.04.2012 and 09.37hrs.  A cable fault of 66kV School Lane Ckt-I of NDMC resulted the tripping of both transformers causing the loss of 200MW generation at GT and interruption of supply occurred in NDMC areas and DMRC networks.

The trippings were analysed in an emergently convened Protection Sub-Committee meeting held on 04.04.2012.  The cause of the trippings were attributed to the problem in control Cable network and Earthing at GT and remote ends stations like School Lane S/Stn of NDMC.

It was also observed that though the transformers are installed at Gas Turbine Station, the control system is provided at Pragati Station about one kilometre away from the transformers.  The control cables even pass under the Railway Tracks.

The Protection Sub-Committee observed that action should be taken immediately to provide control system near to the transformers to avoid such types of indiscriminate trippings due to control cable problems.

Some members of the Protection Sub-Committee were of the view that the Pragati S/Stn of DTL is the main link sub-station of about 600MW generation (270MW GT Station and 330MW Pragati Station) with Grid, the Pragati Station is the ex-bus sub-station of IPGCL / PPCL and hence should be maintained by the agency dealing the generating activities, for proper coordination of maintenance activities and to ensure very essential 600MW generation at load centre having repercussion of electricity supply of VVIP and essential services.

IPGCL representatives strongly objected the idea of handing over the transmission assets of 220/66kV 160MVA Txs installed at GT end to them for maintenance.  They were of the view that these ICTs are meant for evacuation of generation from Gas Turbine generating station which is the responsibility of the Transmission Utility.  They have also expressed their inability to maintain the same due to lack of expertise in maintaining such type of equipments being the transmission elements.

General Manager (O&M)-I was on the stand that the handing over of the assets (220/66kV 160MVA Txs) was proposed for better operational flexibility as the transformers are placed in the GT yard and the control is at IP Ext (Pragati).  He was of the view that the control system of the equipments should be very near to the equipments to avoid such type of indiscriminate trippings.

He further intimated that recently, the following remedial measures were also carried out to avoid the recurring of such types of indiscriminate trippings as suggested by the Protection Sub-Committee :-

a)	Earthing of Control cables armour should have be earthed at one end only.  O&M staff availed the shut-downs on 05.04.2012 and on 09.04.2012 for 66/220kV 160MVA Power Txs no.2 at GTPS.  During shut-down earthing of control cables armour at multiple points were observed and these multiple earthings were removed now these are eartherd at Pragati end only.

b)	The IR value of tripping ckts checked with 500V megger.  The IR values of cores of K63, K65, K67 (OSR, ITI, WTI) were found low (in kΩ).  The same was replaced with spare healthy cores in other cable.  The final IR values of all cores now are in the range of 70-150MΩ.  OTI alarm & tripping have been set at 850C and 950 respectively and WTI alarm & tripping have been set at 900 C & 1000C respectively.

c)	Settings of WTI, OTI and OSR were checked by O&M Staff as per OEM along with exploring possibility of mounting the Marshalling box on separate foundation as the existing mounting arrangement of Marshalling box on the main tank wall might be one false operation of OTI & WTI.

d)	On 09.04.2012 during testing of differential and REF circuitry, low IR values were found in 4 cores of the HV & LV NCT circuitry and the same was attended by replacing with spare healthy cores in other cable.

e)	Similarly on 07.04.2012, a shut-down was availed for 66/220kV 160MVA Power Txs. No.1 at GTPS.  There multiple earthing of the control cable (Marshalling box, Terminal connection points in GTPS yard, one near to Pragati DM Plant and in the other at Pragati switch yard).  These multiple earthings were removed now these are earthed at Pragati end only.

f)	The checking of IR values, OTI & WTI alarm and tripping settings were taken.  IR values were found in the range of 100-150MΩ.

g)	The possibility of separate mounting of Marshalling box of both the transformers is being carried out.

IPGCL representative reiterated their stand already communicated by Director (Technical), IPGCL to DTL that the space for shifting the control of transformers would be provided at GT.

The representative of O&M Department of DTL indicated that if the space is provided for shifting the control system of two transformers and the same is shifted, the O&M expenditure would increase substantially for establishment of control room and providing shift staff etc for operation of two ICTs.

The representatives of Distribution Licensees were univocal that the transformers should be maintained by DTL being the STU of Delhi.  Further for better operational control, the SCADA based control should be implemented so that O&M expenses could be reduced.

Intervening the discussions, Director (Operations), DTL advised that DTL along with all other utilities whose feeders are emanating from GT Station and IPGCL should jointly chalk out the plans to avert the indiscriminate trippings and the causes identified in joint efforts should be rectified as quick as possible.

Concluding the discussions, GCC advised DTL’s concerned  O&M Department to continue the maintenance activities of the 220/66kV 160MVA transformers and immediate steps such as provision of BCU, SCADA based Control be explored for stable operation of load centre based generating stations such as subject Gas Turbine Station and thereby ensuring stable supply to the areas fed from the Station.

12	STRATEGY TO MEET THE IMPLICATIONS OF CLOSING RPH STATION

Due to the environmental stipulation, the State Government has decided to close down coal based generation at RPH.  The closure of the station is deferred till 31.03.2013.

Delhi OCC has been discussing the issue for quite some time.  The Delhi OCC in its meeting held on 25.01.2012 and 29.03.2012 has suggested the following measures to take care of closure of RPH Power Plant.

| Recomendations | Status indicated in OCC meetings. |
| --- | --- |
| DTL to consider the enhancement of transmission capacity than going for LILO of 220kV IP Extn (Pragati) – Sarita Vihar Ckt at 400kV Maharanibagh S/stn as the scheme has not been approved by CEA. In the 1st phase the Transmission Line capacity should be enhanced in the section between 220kV Wazirabad-Geeta Colony- Patparganj-IP-IP Extension (Pragti). This work must be completed before the on set of Summer of 2013. In the 2nd phase the augmentation between 220kV Wazirabad-Mandola (four no of ckt.) and BTPS- Saritavihar (two no of ckt.) should be done. | Planning Deptt. of DTL to confirm the details of Scheme to take care of Generation loss at RPH being the Load Center Station. |
| DTL to install one additional 220/66kV 100MVA Tx or enhance the present 2X100MVA capacity to 2x160MVA capacity at Gazipur to ensure more evacuation of power to take care of loss of generation at RPH in the event of its closure. | PR to be sent by Project Deptt. to Store Deptt. of DTL. Excpected by Dec.12. |
| Early completion of 220kV Maharani Bagh- Gazipur ckt. by DTL | Work should be carried out as quickly as possible for stability of supply to East Delhi. |
| SLDC to take up with the State Government for deferring the closing of the RPH till 31.03.2013 so that DTL can enhance the transmission capacity to take care of the generation loss of RPH by the time, otherwise continuous load shedding would be inevitable in Central and East Delhi areas during summer months. | IPGCL has already initiated the step to continue the operation of Rajghat Power House till 31.03.2013. |

220/33kV 100MVA Tx. has been commissinoed at RPH on 17.04.2012 at 16.10hrs.  and load taken on 19.04.2012 at 13.10hrs (the transformer was out from 13.53hrs. on 10.07.2011 due to damage).

In the Delhi OCC meeting held on 29.03.2012, Delhi OCC requested DTL to take  suitable action so that a time lined startegy is implemented to meet the impending closure of RPH and requested that the above mentiondc augmentation of Transmission Capacity be completed before the on set of next summer for ensuring the stable and realible supply to East,Central and NDMC areas of Delhi.

In addition to above, as a Long Term Measure, establishment of Second Source at RPH via 400kV East of Loni Road (Harsh Vihar) -Wazirabad – Kasmirigate – RPH should be done for stable supply to East,Central and NDMC areas of Delhi.

The representative of Planning Department of DTL informed that they have already started the process of installation of 220kV GIS Station at RPH for which site inspection etc has already been carried out.  The endeavour is the establishment of 220kV GIS Station without waiting for the closure of the generating plant at RPH.  The augmentation of transmission line capacity has already been covered under the Business Plan for the period 2012-17.  The section between Wazirabad to Maharani Bagh would first be covered under the scheme though it was planned from 2014-15 onwards, the same would be preponed from 2012-13 onwards.  In the meanwhile all out efforts would be taken to establish the 220kV link between Maharani Bagh and Gazipur.

Efforts are also on for establishment of Anand Vihar 220kV S/Stn with the in feed from upcoming 400kV Harsh Vihar S/Stn.  The inter connection of Harsh Vihar to Wazirabad S/Stn is also planned.

BYPL representative opined that without establishing the systems as suggested by Operation Coordination Committee if the load centre based generating station i.e. Rajghat is closed down, power crisis would definitely be surfaced in the areas fed from Rajghat S/Stn particularly the Central Delhi areas.

Concluding the discussion, GCC advised DTL’s Planning Department to immediately start the processing of enhancement of transmission line capacity between Wazirabad to Maharani Bagh as the short term measure and quickly devise the schemes suggested by Delhi OCC to take care of the impending closure of RPH Station.

13	WORK OF REPLACEMENT OF PORECELAIN INSULATORS WITH POLYMER AND REPLACEMENT OF CONDUCTORS OF 220KV NARELA – ROHTAK ROAD TRANSMISSION LINES OWNED BY BBMB.

TPDDL put up the agenda.  The matter has been monitored by Delhi OCC in its regular meetings.  The brief history of the issue is given hereunder :-

220kV Sub-Station of Rohtak Road is of BBMB S/Stn

This Grid is having three 220/33kV 100MVA transformers and one 220/66kV 100MVA transformer.  Further, there is one 66/33kV 50MVA transformer.  The 33kV bus capacity at Rohtak Road is restricted to 1250Amps.  As such at a time, only two 220/33kV transformers are kept in service.  There are four 33kV inter connection feeders to feed the 33kV Rohtak Road S/Stn of TPDDL.  The 220kV Rohtak Road S/Stn is fed through 220kV Ckts. from Narela S/Stn of DTL.  These circuits are of GOAT Conductors and about 60 years old.  The total capacity of the double circuit is 125MW.  The conductors of the circuits are required to be replaced for enhancing the drawal capacity of Delhi system from Rohtak Road S/Stn.  The replacement of existing porcelain disc insulators with porcelain insulators are also required to be carried out to avoid trippings in fog.

For maintaining the supply from Rohtak Road, the charges are being paid by Delhi Discoms BRPL, BYPL and TPDDL from 01.04.2007.  Before that DESU/DVB / DTL was paying.  The rates were fixed 1.25Lacs per months during the period 01.04.1987 to 31.03.1997.  The same was enhanced to Rs. 5.5 Lacs per month from 01.04.1997 to 30.09.2003 which was further increased to Rs.8.10Lacs per month from 01.10.2003.  The increment was mainly to meet the requirement of augmentation of 220kV Narela – Rohtak Road lines and bus bars at Rohtak Road S/Stn.   In the last OCC meeting also, it was indicated that the augmentation of the conductors would be carried out along with work of replacement of insulators.  DERC is also hearing the matter of charges and enhancement of capacity in a petition no. 72/2008 filed by TPDDL.

TPDDL has taken the matter in the 74th OCC meeting of NRPC held on 17.04.2012 wherein the representative of BBMB had stated that tenders invited by BBMB for augmentation of the conductors of 220kV Rohtak Road – Narela Ckts. along with replacement of porcelain insulators with polymer insulators. But the tenderors do not meet the evaluation criteria.  It was further stated that for replacement of conductors, the tendering was done twice, first time, no body quoted, and second time, two vendors quoted but work could not be awarded.  To decide the issue of further course of action, the internal meeting of BBMB is being arranged.

In NRPC meeting, TPDDL representative further suggested the reinforcement of BBMB Rohtak Road Grid S/Stn from a source like Mundka as at present 220kV Rohtak Road S/Stn has only one feed i.e. through 220kV Narela – Rohtak Road Double Circuits for which NRPC advised TPDDL to take up the matter with CEA along with DTL.

Concluding the discussions, GCC requested Chairperson, GCC to take up the issue at Chairperson / Member level of BBMB to sort out the issue of augmentation of transmission line capacity of 220kV Narela – Rohtak road Double Ckt line and augmentation of 33kV Buses for enhancing the infeed capacity for better utilization of available resources.

14	DATA DISCREPANCY BETWEEN ACTUAL DRAWAL OF TPDDL AND SCADA DATA OF SLDC.

TPDDL representative mentioned about the discrepancies in actual real time load data of TPDDL.  He requested for updation of real time scheduling and actual data indicating the drawal of various utilities to effective control.

SLDC representative explained that as per Connectivity Regulations notified by CEA, IEGC and DGC, the required data provision to SLDC is the responsibility of Discoms and Generating Utilities.

He further clarified that in spite of protracted discussions, the same has not been done in the case of Discoms.  Now, it has been decided that the Discom data is to be linked through ICCP Server to SLDC and Disoms’s data integration is envisaged to be implemented in the establishment of ULDC Phase-II being established by PGCIL as uniformly in the Northern Region.  Till the establishment of real time data connectivity by the available facility of using RTUs / Transducers of ULDC Phase-I is being used to compute the actual drawal of Discoms.  Since the real time data facility is available only upto 66kV (in some cases 33kV) level at present, the computation of actual drawal of Discoms may not be so accurate with that of actual drawal.  The analysis shows that the variation is +10%.  Once, the ICCP server integration is established, the variation would definitely be reduced considerably.

At present, the TPDDL’s actual load data on real time basis is computed as under :-

POSITION AT 11.30HRS. ON 12.04.2012

| DRAWAL CALCULATION OF NDPL ON REAL TIME BASIS |
| --- |
| Station | Feeder / transformer | MW | Station | Feeder / transformer | MW |
| Gopalpur | EB_T1 | 35.89 | Kashmiri Gate | 220kV DMRC-1 | 0.00 |
|  | EC_T2 | 35.89 |  | 220kV DMRC-2 | 0.00 |
|  | EB_T3 | 26.95 |  | B_CIVILLN_KGAT | 0.00 |
| Subzi Mandi | EB_T1 | 39.54 |  | B_CIVILLN_KGAT | 0.00 |
|  | EB_T2 | 24.80 | Rohtak Road | B_RHTK_RMPURA1 | 50.69 |
| Shalimar Bagh | EB_T1 | 38.87 |  | B_RHTK_RMPURA2 |  |
|  | EB_T2 | 37.68 |  | B_RHTK_SH.W.BAGH1 |  |
|  | EB_T3 | 45.72 |  | B_RHTK_SH.W.BAGH2 |  |
|  | 220kV DMRC | 7.30 |  | A_RHTK_24BLK MOTINGR |  |
| Narela | EC_T1 | 45.90 |  | A_RHTK_AMARPRK |  |
|  | EC_T2 | 51.49 |  | Local Tr. |  |
|  | EC_T3 | 26.47 |  | A_I/D MOTINAGAR |  |
| Bawana | EC_ST2 | 67.16 | DSIDC | EC_T2 | 3.05 |
| Kanjhawala | EC_T1 | 30.01 |  | EC_T3 | 64.85 |
|  | EC_T2 | 15.71 |  | B | 118.60 |
| Shastri Park | Pusa Grid-I | 4.90 | EXPORT TO BSES YAMUNA |
|  | Pusa Grid-II | 5.00 | SUBZI MANDI | B_BGROAD_SUBZI1 | 0.00 |
| DMS | B_DMC_Pandav Nagar | 0.16 |  | B_BGROAD_SUBZI2 | 2.34 |
| Sudershan Park | A_Vishal_SUDRSN1 | -4.80 | EXPORT TO BSES RAJDHANI |
| Rewari Line | 33kV Bus Coupler | 0.00 | MANGOLPURI (BOTH MTRS) | NANGLOI-1 | 12.00 |
|  | Tx-2 | 0.08 |  | NANGLOI-2 | 10.00 |
| Naraina | B_NRINA_REWAR1 | 10.54 |  | C | 24.34 |
|  | B_NRINA_REWAR2 | 9.24 | TOTAL DRAWAL OF NDPL (A+B+C) | 821.88 |
|  | B_NRINA_INDERPURI | 6.27 |  |  |
|  | BA_T1 | 3.00 |  |  |
|  | BT_T2 | 5.00 |  |  |
| Rohini | EC_T1 | 43.63 |  |  |
|  | EC_T2 | 44.53 |  |  |
|  | EC_T3 | 36.71 |  |  |
|  | EC_T4 | 33.58 |  |  |
| A | 727.62 | 727.62 |  |  |

In the above computation, 61MW load is taken as in total of all feeders given hereunder based on actual computation of SEMs :-

Fixed data

| Name of the Grid | Name of feeders |
| --- | --- |
| DMS | Shadikhampur |
|  | 69 MG Road |
|  | Breakfast |
|  | Philips |
|  | Pandav Nagar |
|  | `J’ Block Kirti Nagar |
|  | `H’ Block Kirti Nagar |
| BG Road | Sadar |
|  | CSA |
|  | DCM-II |
|  | MG Road |
|  | Moti Nagar-II |
|  | 53 Rama road |
|  | Breakfast |
|  | Rama Road |
| Mundka | Mangolpuri T-Off Nangloi |
|  | 66kV Mangolpuri |
| Faiz Road | Tibbia College-I |
|  | Tibbia College-2 |
|  | Tibia Nanakpura |
| S.B. Mills | Philips |
|  | Moti Nagar |
| Shastri Park (Central) | Pusa Road Ckt-I |
|  | Pusa Road Ckt-II |
| Sudershan Park | Vishal |
| Rewari Line | Bus Coupler |
| Kashmiri Gate | ISBT |
|  | 20MVA Tx. |
|  | 11kV Bus coupler |
| Ghewra | LILO Mangolpuri – Nangloi |
| Vishal | Bali Nagar |
|  | ESI |
|  | Ramesh Nagar |
| Naraina | Local Tx-I |
| Gopalpur | Local Tx-II |
| Narela | Local Tx-I |
| Rohini | Local Tx-I |
| Shalimar Bagh | Local Tx |
| Kanjhawala | Local Tx-I |
| Subzi Mandi | Local Tx-I |
| DSIDC Bawana | Local Tx-I |
| Kanjhawala | 66kV DMR Mundka |
| Total | 61MW (at 11.30hrs. on 12.04.2012) |

TPDDL representative requested to update the status of fixed data computations based on SEM data atleast on quarterly basis to have actual drawal close to the real value.  He agreed to cooperate with the SCADA circle of SLDC for updation.

Other Distribution Licensees representatives also echoed the same views of the TPDDL.

SLDC agreed for incorporating the latest trend of fixed data points based on SEM data in computing real time drawal of Distribution Licensees in coordination with all concerned.

15	GUIDELINES TO BE ISSUED BY STU (DTL) WITH REGARD TO INTRASTATE OPEN ACCESS IN DELHI.

DERC vide its notification dated 3rd January 2006 fixed the terms and condition for Open access in Delhi. As per Clause 5(2) of the regulations the delivery of electricity for use by consumers with connected load of 1MW and above through open access route is fixed at 1st July 2008.

As per Clause 10(4) of the regulation, STU (DTL) has to draw out Procedure for implementation of Open Access. The relevant portion of the regulation is reproduced hereunder :-

- The Nodal Agency shall decide on the capacity available or the existence of operational constraints, consistent with the principles and guidelines as decided by the State Transmission Utility. The State Transmission Utility shall decide such principles within thirty days of publication of these Regulations.”

Chairperson GCC constituted a Committee under the Chairmanship of Executive Director (T), DTL vide letter dt. 20.05.2011 comprising the representatives of distribution licences, Generating Stations, DTL, SLDC & DERC to draw out guidelines for implementation of Intrastate Open Access in Delhi. The Committee met thrice to finalize the guidelines.  The draft procedure were finalized considering the Open Access customers as embedded customers of the Distribution Licensees though they source power other than the concerned Distribution Licensees as they avail all infrastructure of the Distribution Licensee.  The Distribution Licensees were of the view that they are not obliged to supply power to the consumers whose connected load is 1 MW or more as per the latest Central Govt. directions as such type of consumers are deemed open access consumers.

It was decided to place the procedure before the Commission for its consideration and approval.  Accordingly the procedure was submitted to DERC for the consideration.

Sh. Ajay Kumar, Vice President, BRPL opined that the report sent by the Chairperson of the Committee outlines only the sentiments of SLDC in the issue.  Even though, the views of various Stakeholders have been mentioned in the Annexure of the covering letter, but it has not been highlighted in the main body of the letter.  He requested for another communication from Chairperson of the Committee to the Commission highlighting the issues raised by the Stakeholders with regard to the guidelines.

TPDDL representative mentioned that they have already informed the Commission to the extent of disagreement with regard to each clauses.  He further mentioned that the views of other representatives of Distribution Licensees seem to be same in the issues pointed out by TPDDL.

SLDC representative readout the entire text of the main body of the letter forwarding the procedures send to DERC and explained that adequate mentioning has been done regarding the extent of disagreement of Stakeholders.

DERC representative was of the view that since the Committee has already done its job and requested the Commission to address the issue mentioned by the Stakeholders and requested to wait for the decision of the Commission.

Chair also expressed the same view of the DERC representative and hoped that the Commission would address the issues pointed out in the report soon.

COMMERCIAL ISSUES.

14.	FINALIZATION OF METERING PROCEDURES

As per Clause 31.1 of Delhi Grid Code, STU has to draw out the Metering Procedure and get it approved from DERC before implementation.

The draft Metering Procedures drawn out based on the discussion held on 22.08.2008, at BTPS, 06.10.2008 & 10.10.2008 at SLDC was put up for approval in the second meeting of GCC held on 25.11.2008. However, the Metering Procedures were referred back to metering committee which had not considered the revised Metering Regulations of CEA.  CEA vide their notification dt. 04.06.2010 amended the principal Regulation with regard to Installation of Operation of Meters Regulations 2006 issued on 17.03.2006.

The Metering Committee in its 3rd meeting held on 15.06.2011 approved the Metering Procedures and decided to put up for approving to GCC for its approval.

GCC approved the Metering Procedure finalized by the Metering Committee and advise DTL’s concerned O&M Department dealing Metering subject to forward the procedures to DERC for its approval.  It was further advised that after the approval of the Commission, the same may be posted in the website of STU.  The Metering Procedure approved by GCC is enclosed as Annexure-4.

15	Incentive based on TRANSMISSION System availability of Delhi Transco LIMITED for 2010-11

Multi Year Tariff (MYT) Transmission Regulations notified by DERC allows the Transmission utility to recover incentive if it achieves more than target availability fixed for its purpose. The details for the Transmission Tariff Regulations are extracted as under :

Clause 5.30 of the Multi Year Transmission Tariff Regulations 2007 applicable upto 31.03.2012, the incentive clause is specified as under :-

“Operational Norms

5.30.	The Commission shall specify suitable norms of operation for the Transmission Licensee in the Multi Year Tariff Order, based on the submission of the Business Plans.  The parameter which shall be considered would cover, among others;

a)	Transmission System Availability : The Target Availability for recovery of full annual transmission charges during the Control Period shall be 98%.

Incentive

The Transmission Licensee shall be entitled to incentive on achieving annual Availability beyond this Target Availability, in accordance with the following formula:

Incentive	=	ATSC *  [AA – TA]

[TA]

Where ATSC is the Annual Transmission Service Charge corresponding to the assets of the Transmission Licensee;

TA is the as Target Transmission System Availability (in percent) as defined in Clause 5.3(a);

AA is the actual Annual Availability (in percent) of the transmission system of the Transmission Licensee;

Provided that no incentive shall be payable above the Availability of 99.75%”

5.31	Incentive shall be shared by the Beneficiaries in the ratio of their Allotted Transmission Capacity for the year.

Clause 5.3(a) of the transmission tariff regulations clarifies

“Transmission System Availability: The Target Availability for recovery of full annual transmission charges during the control period shall be 98%”

The Transmission System availability of DTL for the year 2010-11 has been worked out by SLDC in consultation with the Stake holders and based on guide lines issued by DERC during January 2004 as under:

| AVAILABILITY OF DELHI TRANSCO LIMITED SYSTEM FOR THE YEAR 2010-11 |
| --- |
| Sl. No. | Name of Elements | Availability in %age |
| 1 | AVAILABILITY OF 8NOS. 400kV, 315MVA ICTs | 94.46% |
| 2 | AVAILABILITY OF 10NOS. 400kV LINES | 99.57% |
| 3 | AVAILABILITY OF 72NOS. 220kV LINES | 99.19% |
| 4 | AVAILABILITY OF 49NOS. 220/66kV ICTs | 96.53% |
| 5 | AVAILABILITY OF 30NOS. 220/33kV ICTs | 92.06% |
| 6 | AVAILABILITY OF 3NOS. 66/33kV ICTs | 98.48% |
| 7 | AVAILABILITY OF 24NOS. 66/11kV PR. TXS | 99.68% |
| 8 | AVAILABILITY OF 16NOS. 33/11kV PR. TXS | 98.23% |
| 9 | AVAILABILITY OF 105NOS. 66kV FEEDER BAYs | 99.90% |
| 10 | AVAILABILITY OF 119NOS. 33kV FEEDER BAYs | 99.89% |
| 11 | AVAILABILITY OF 204NOS. 11kV SYSTEM | 100.00% |
| 12 | AVAILABILITY OF 59NOS. CAP. BANKS | 93.04% |
| TOTAL AVAILABILITY OF DTL SYSTEM = |  |
| 94.46*8+99.57*10+99.19*72+96.53*49+92.06*30+98.48*3+99.68*24+98.23*16+99.90*105+99.89*119+100*204+93.04*59 |
| 8+10+72+49+30+3+24+16+105+119+204+59 |
|  | = 98.58% |  |

Based on the MYT Regulations, the Transmission Tariff approved for 2010-11 as per the order of the commission dt. 26.08.2011 are Rs. 532.94Crs. (refer page no. 68 table no. 54 of the order of the Commission)

(a) 	Annual Transmission Service Charges (ATSC)		=Rs. 532.94Crores

for 2010-11

(b) 	The normative target availability for recovery of full	=98%

transmission tariff as mentioned in (a) in %

(c)	 Transmission System Availability achieved by DTL	= 98.58%.

(d) 	Incentive =ATSC* [AA – TA] = 532.94*[98.58-98.00]	=Rs. 3.1541347rore

[TA]		             [98.00

It was further pointed out in the Agenda, the Transmission System Availability was inadvertently mentioned as 98.98% and the incentive was accordingly calculated.  It has been confirmed that the actual reconciled Transmission System Availability is 98.58%.  As per the Multi Year Transmission Regulations, the incentive earned by the Transmission Utility is to be borne by the beneficiaries in the ratio of Transmission capacity allocation. The Transmission capacity allocation for 2010-11 has been worked as under:

Details of Transmission Capacity allocation for FY 2010-11

All figures are in %

| Month | Name of the beneficiaries |
| --- | --- |
|  | BRPL | BYPL | TPDDL | NDMC | MES | Total |
| Apr'10 | 41.25 | 26.30 | 25.51 | 5.97 | 0.98 | 100.00 |
| May'10 | 39.61 | 26.00 | 27.78 | 5.71 | 0.90 | 100.00 |
| June'10 | 38.75 | 26.09 | 28.13 | 6.04 | 0.99 | 100.00 |
| July'10 | 41.47 | 25.88 | 26.40 | 5.39 | 0.86 | 100.00 |
| Aug'10 | 41.25 | 26.30 | 25.51 | 5.97 | 0.98 | 100.00 |
| Sept'10 | 42.28 | 26.03 | 25.74 | 5.13 | 0.82 | 100.00 |
| Oct'10 | 41.37 | 24.99 | 26.97 | 5.74 | 0.93 | 100.00 |
| Nov'10 | 40.30 | 25.87 | 26.77 | 6.06 | 1.00 | 100.00 |
| Dec'10 | 40.28 | 25.80 | 26.84 | 6.08 | 1.00 | 100.00 |
| Jan'11 | 41.95 | 25.09 | 26.08 | 5.91 | 0.97 | 100.00 |
| Feb'11 | 40.30 | 25.86 | 26.75 | 6.09 | 1.00 | 100.00 |
| Mar'11 | 40.35 | 25.88 | 26.80 | 5.99 | 0.99 | 100.00 |
| Total | 40.76 | 25.84 | 26.61 | 5.84 | 0.95 | 100.00 |

Accordingly, to the incentive for 2010-11 has to be recovered from the Licensees as under :

| Sl. No. | Distribution Licensees | Capacity allocation for 2010-11 in % | Amount of Incentive to be recovered in Rs. Lacs |
| --- | --- | --- | --- |
| 1 | TPDDL | 26.61 | 83.93152 |
| 2 | BRPL | 40.76 | 128.56253 |
| 3 | BYPL | 25.84 | 81.50284 |
| 4 | NDMC | 5.84 | 18.42015 |
| 5 | MES | 0.95 | 2.99643 |
|  | Total | 100 | 315.41347 |

GCC approved the Transmission System Availability of DTL as 98.58% as reconciled with the Stakeholders for the year 2010-11.

16	DELHI STU CHARGES FOR OPEN ACCESS TRANSACTIONS FOR 2012-13.

SLDC representative clarified the issue as under :-

Clause no. 6.7 of the MYT regulations of DERC notified on 30.05.2007 valid for the period 01.04.2007 to 31.03.2012 stipulates the rates for STU charges of Delhi for short term open access transactions as under : -

6.7 	In the case of Short Term Open Access Customers, charges payable shall be calculated in accordance to following methodology:

ST_RATE = 0.25 x [ATSC/ Av_CAP]/ 365;

Where:

ST_RATE is the rate for short-term open access customer in Rs per MW per day;

ATSC is Annual Transmission Service Charge;

Av_CAP means the average capacity in MW served by the transmission system of the Transmission Licensee in the last Financial Year and shall be the sum of the generating capacities connected to the transmission system and contracted capacities of other transactions handled by the system of the Transmission Licensee;

6.8 25% of the charges collected from the Short Term Open Access customer shall be retained by the Transmission Licensee and the balance 75% shall be adjusted towards reduction in the transmission service charges payable by the Beneficiaries.”

The MYT Regulation in respect of Transmission Tariff for the period 01.04.2012 to 31.03.2015, the STU Charges for Open Access is regulated as under :-

6.11 	No distinction in charges shall exist in terms of long term, medium term or short term access to the intra-State Transmission System.

Provided that, the transactions for long term and medium term shall be denominated in Rs/kW/month or any suitable denomination as may be stipulated by the Commission.

6.12 	For short term bilateral transactions and short term collective transactions through power exchanges, the transmission tariff shall be denominated in Rs/kWh/hr.

Since, no methodology has been devised for computation of STU Charges for open access transactions by the State Commission in the Transmission Tariff Regulation, the Central Electricity Regulatory Commission (Open Access in Interstate Transmission) Regulations would be made applicable.  As such, SLDC proposed Rs. 110/MWh as STU Charges for the transactions from 01.04.2012 as per the provisions of CERC Regulations 2008, which are charges applicable for drawal and injection charges of Delhi of PoC regime.  SLDC quoted relevant provisions of CERC (Open Access) Regulations 2008 as under :-

Transmission Charges

16(1)	In case of bilateral transactions, for use of the inter-State transmission system, the transmission charges at the rate specified hereunder shall be payable by the applicant for the energy approved for transmission at the point(s) of injection:

Type of Transaction Transmission charges		(Total) (Rs./MWh)

(a) 	Bilateral, intra-regional 					30

(b) 	Bilateral, between adjacent regions 			60

(c) 	Bilateral, wheeling through one or more 			90

intervening regions

(2) 	In case of the collective transaction, for use of the inter-State transmission system, transmission charges at the rate of Rs.30/MWh for energy approved for transmission for each point of injection and for each point of drawal shall be payable.

(3) 	The intra-State entities shall additionally pay transmission charges for use of the State network as determined by the respective State Commission:

Provided that in case the State Commission has not determined the transmission charges, the same shall not be a ground for denial of open access and charges for use of respective State network shall be payable for the energy approved at the rate of Rs.30/MWh:

Provided further that transmission charges for use of the State network shall be intimated to the Regional Load Despatch Centre concerned for display on its web site:

Provided also that transmission charges shall not be revised with retrospective effect.

Now, from 01.07.2011, Point of Connection (PoC) charges are enforced for CTU Charges.   CERC vide order dated 31.03.2012 has determined the PoC Charges of Delhi for injection and withdrawal as Rs.80000/MW/month for long term and 11Ps/Unit for short term transactions for the period April 2012 to September 2012.

Since, there is no methodology to compute the STU Charges of Delhi for Open Access purpose from 01.04.2012 has been specified by DERC, all RLDCs and Power Exchanges was requested to apply the STU charges of Delhi as 11Ps / kWh i.e. Rs. 110/MWh for the open access transactions starting from 01.04.2012 whose applications are received on or after 01.04.2012, in line with the CERC order 31.03.2012 fixing the PoC charges for drawal and injection for Delhi.

However, NLDC has indicated that there is an amendment of Open Access Regulations in 2009 of CERC wherein it is mentioned that in case, no charges are fixed by State Electricity Regulatory Commissions for STU usages for Open Access purposes, the charges would be Rs. 80/MWh.  Accordingly, from 2012-13, the STU Charges for Open Access in respect of Delhi is fixed at Rs. 80/MWh from 03.04.2012.  The relevant clause of CERC amended CERC Regulations is of Open Access reproduced hereunder :-

10. 	Amendment of regulation 16 - Regulation 16 of the principal regulations shall be substituted as under, namely-

“Transmission Charges

16. (1) In case of bilateral transactions, the transmission charges at the rate specified hereunder shall be payable by the short-term customer for the energy approved for transmission at the point or points of injection:

Type of Transaction Transmission charges(Total) (Rs./MWh)

(a) 	Bilateral, intra-regional 			80

(b) 	Bilateral, between adjacent regions 	160

(c) 	Bilateral, wheeling through one or more 	240

intervening regions

(2) 	In case of the collective transactions, transmission charges at the rate of Rs. 100/MWh for energy approved for transmission separately for each point of injection and for each point of drawal, shall be payable.

(3) 	The intra-State entities shall pay the transmission charges for use of the State network as fixed by the respective State Commission in addition to the charges specified under clauses (1) and (2):

Provided that in case the State Commission has not determined the transmission charges, the charges for use of respective State network shall be payable at the rate of Rs.80/MWh for the electricity transmitted:

Provided further that non-fixation of the transmission charges by the State Commission for use of the State network shall not be a ground for refusal of open access:

Provided also that the transmission charges payable for use of the State network shall be conveyed to the Regional Load Despatch Centre concerned who shall display these rates on its web site:

Provided also that the transmission charges payable for use of the State network shall not be revised retrospectively.”

GCC noted the STU Charges of Delhi as Rs80/MWh for Open Access purposes till the State Commission decides the STU Charges for Open Access from 03.04.2012 as indicated by NRLDC in their communication dated 20.04.2012.

17	Scheduling and associated issues of 16MW Generating Unit of Timapur – Okhla Waste Management Company Pvt Ltd, Okhla Plant.

SLDC representative briefed the issue as under :-

A 16MW Power Plant has been established by a generating company namely Timarpur- Okhla Waste Management Company Pvt Ltd (TOWMCL) at Okhla.  The generation of the plant is delivered at 33kV bus of 66kV Jasola S/Stn of BRPL.  50% of the generation (60MUs per year) is available for sale to BRPL at a rate arrived through competitive bid.  The balance power can be sold to third party by the generating company through Open Access route.  On the request of both parties, BRPL & TOWMCL, two coordination meeting were held at – one at SLDC on 10.02.2012 and other at Plant site (Okhla) on 03.04.2012. The gist of the discussions and decisions taken in the meetings are as under:-

i)	There are three boilers out of which the two boilers are commissioned.  The third boiler is expected to be commissioned by this month end.  After the commissioning of the third boiler, the station would be declared as under commercial operation.  The station is delivering infirm power from 27.01.2012.  In the first meeting held on 10.02.2012 at SLDC, it was decided to treat the generation injection at Jasola S/Stn by the generating plant would be treated at Infirm power and charged at UI Rate.  In the meeting held on 03.04.2012, it was decided that payment of ‘infirm power’ would be adjusted with BRPL as the power is consumed by them.

ii)	After commissioning the unit in commercial operation, the transaction would be as per PPA.  As per PPA, BRPL should facilitate the transaction of power more than 50% of the generation for sale to third party by the company.  Both parties were advised for arriving the agreement for transaction of the power consumed by BRPL for more than 50% of quantum.  Since, both parties could not find any amicable solution, they were given 15 days time failing which the meeting held on 03.04.2012 at Okhla Plant and decided the following methodology:-

TOWMCL can sale the power to third party of 50% of the capacity after meeting the auxiliary requirement i.e. 6.24MW on day ahead basis after the COD of the station.  This power could be traded by the generating company through open access. Once the power is sold through open access route, UI needs to be applied for mismatched energy of TOWMCL power.  To meet the criteria of Must Run, the schedule for open access could be fixed on the basis of 50% of the actual generation converting into 15 minutes time block and match with scheduled quantum for open access and UI would be made applicable for the mismatched quantum as per the UI regulations.

Such mismatch and corresponding UI amount could be deducted from the billed amount for 50% generation to BRPL as per the PPA at a settled rate, on monthly basis. The proposed methodology is on the basis of the fact that the generator is located in the BRPL’s controlled area and the entire generation of the power station is consumed locally by the utility. Any variation of generation gets automatically affected the BRPL’s drawal from the grid and imposition of corresponding UI which is proposed to be adjusted in the bill of the generator.

In case the generator goes for open access for the sale of 50% quantum available with it the following charges are required to be paid by the generator who is obviously being the applicant for the sale of energy.

| Sr. No. | Component of Open Access | Charges (Rs.) | Remarks |
| --- | --- | --- | --- |
| 1 | Application Charges | 5000 per application | If the sale is to the intrastate utilities within Delhi to be paid to SLDC. For the purpose of interstate transactions the same would also be given to SLDC for consent of the such transactions. |
| 2 | Scheduling charges for SLDC, Delhi | 2000 per day | If the sale is to the intrastate utilities within Delhi to be paid to SLDC within three days after the approval of the open access on monthly basis. For the purpose of interstate transactions the same would be charges by the nodal RLDC and reimburse the same to SLDC Delhi. |
| 3 | STU Charges of Delhi | 80 per MWh | If the sale is to the intrastate utilities within Delhi to be paid to SLDC within three days after the approval of the open access to Delhi SLDC. SLDC shall reimburse the same to DTL on monthly basis after the receipt of the amount. For the purpose of interstate transactions the same would be charges by the nodal RLDC and reimburse the same to SLDC Delhi/ DTL. |
| 4 | Wheeling charges | 31.1 per MWh | To be paid directly to BRPL within 3 days after the approval of the open access. The rate is based on the retail tariff order of DERC dt. 26.08.2011 for BRPL for the FY 2011-12 and continue the same till the change based on the order for FY 2012-13. |
| 5 | CTU charges | 110 per MWh (only for Delhi injection) | Applicable for interstate transaction only. The drawal charges would be as per the drawal point. The collection and disbursement lies within the responsibility of nodal RLDCs. |

| Sr. No. | Component of Open Access | Charges (Rs.) | Remarks |
| --- | --- | --- | --- |
| 6 | Cross subsidy charges | Nil | Being the generator |
| 7 | Additional surcharge | Nil | Being the generator |
| 8 | Losses (in form of kind) |  |  |
| (i) | STU losses of Delhi | 1.25% |  |
| (ii) | Wheeling losses (BRPL) | 1.40% |  |
| (iii) | CTU losses (for Delhi injection) | 2% | Varies on weekly basis |
| (iv) | CTU Drawal losses | 1.53% -4.3% | Varies on weekly basis and on drawal point |
| (v) | Other state losses | Depend upon the drawal point |

In case the generator could not get any buyer for the 50% capacity allowed for sale to the third party that quantum would obviously be treated as a transaction under UI and same would be adjusted on monthly basis based on the accounts prepared by SLDC based on the meter readings to be provided by STU i.e. DTL for computing actual Ex-bus generation (received at 33kV side of Jasola 66kV S/stn of BRPL).

iii)	TOWMCL was advised to get the generating plant registered with Delhi SLDC as per provision of Clause 3(2) of DERC (Levy and Collection of Fee & Charges of SLDC) Regulations dated 18.10.2007.

iv)	The charges for using auxiliary needs of the stations after the synchronization i.e. 11.16hrs on 27.01.2012 would be charged at UI rate of 15 minutes if the drawal data is provided by company to DTL’s Metering Department for incorporating the drawal and injection for the power plant for preparation of applying UI rate in 15 minutes time block.  This was the same methodology adopted in case of Bawana CCGT.

v)	The real time generation data would be provided by the Station to SLDC.  Though a method worked out with SLDC without jeopardising the existing data system.

BRPL vide their letter dated 16.04.2012 has indicated that they are not agreeable to the decision of the above said meetings.  However, as per the decision of the meeting, TOWMCL has registered as a ‘USER’ with Delhi SLDC on 19.04.2012.  Delhi SLDC has issued bills for infirm power for January 2012 and February 2012 on 20.04.2012.  Later on accounts of Infirm Power for March 2012 was also issued.  As per the decision of the meeting held on 03.04.2012, BRPL has to settle the payment as per the accounts issued by SLDC for infirm power.

Sh. Ajay Kumar, Vice President, BRPL strongly objected the decision taken in the meeting and termed the decision as arbitrary decision of the Committee though in the meeting held on 03.04.2012, the BRPL representative did not agree to the decision.  He further emphasized that TOWMCL should come forward for amicable solution first with them, then request SLDC for settling the accounts etc.  He was of the view that before proceeding further in this matter, decision on embedded generators within the Distribution Company should be taken.  He was of the view that the issues mentioned by the Distribution Companies in Intrastate Open Access Guidelines should first be decided and after that the issues would automatically get resolved in case of TOWMCL.  He was further of the view that TOWMCL should be treated as Open Access Generator in a Distribution Company and the accounts settlements have to be done as a separate entity by SLDC.

SLDC representative objected to the suggestion of BRPL.  He was of the view that the matter be referred to the Commission for a solution and was of the view that the considered decision of the meeting held on 03.04.2012 at TOWMCL should be honoured by BRPL for overall interest of the system.

TOWMCL representative was not present in the meeting and hence their version could not be ascertained.

As no consensus was arrived at, the Chair advised BRPL to resolve the issue in consultation with TOWMCL and inform SLDC and if required, one more meeting could be convened in SLDC after arriving the consensus with BRPL and Generating Company.

18	PAYMENT OF NRLDC CHARGES – PENALY BILL RAISED BYNRLDC FOR THE PERIOD OCTOBER 2010 TO FEBRUARY 2011.

SLDC representative gave a brief background on the issue as under :-

CERC vide notification dated 18.09.2009 notified RLDC Fees and Charges Regulations.  CERC vide order dated 11.03.2011 fixed the NRLDC Charges for the period 01.10.2010 (from the date of creation of Power System Operation Corporation as a 100% subsidiary company of PGCIL) to 31.03.2014.  The relevant portion of regulations stipulating SLDC can be a nodal agency for collection and disbursal of RLDC Fees and Charges are reproduced hereunder :-

22. 	Collection of SOC.-

(1) 	The System operation charges shall be collected from the users as per the norms given below:-

(i) 	Inter state transmission licensees: 10% of system operation charges;

(ii) 	Generating stations and sellers: 45% of system operation charges;

(iii) Distribution licensees and buyers: 45% of system

operation charges.

(2) 	The system operation charges shall be levied on the inter state transmission licensees on the basis of the ckt.-km of the lines owned by them as on the last day of the month prior to billing of the month.

(3) 	The system operation charges from the generating companies and sellers shall be collected in proportion to their installed capacity or contracted capacity, as the case may be, as on the last day of the month prior to billing of the month.

(4) 	The system operation charges from distribution licensees and buyers shall be collected in proportion to the sum of their allocations and contracted capacities, as the case may be, as on the last day of the month prior to billing of the month.

Provided that the respective State Load Despatch Centre shall be the nodal agency for this purpose in the State if the concerned Regional Load Despatch Centre, State Load Despatch Centre and the distribution licensees arrives at a mutual consensus to do so. The respective State Load Despatch Centre shall collect the system operation charges from the distribution licensees within a state on behalf of the concerned Regional Load dispatch Centre and the same shall be deposited to the concerned Regional Load Despatch Centre.

(emphasis supplied)

23. 	Collection of Market Operation Charges

The market operation charges shall be collected equally from all the users except inter state transmission licensees:

Provided that the respective State Load Despatch Centre shall be the nodal agency for this purpose in the State if the concerned Regional Load Despatch Centre, State Load Despatch Centre and the distribution licensees arrives at a mutual consensus to do so. The respective State Load Despatch Centre shall collect the market operation charges from the distribution licensees within a state on behalf of the concerned Regional Load dispatch Centre and the same shall be deposited to the concerned Regional Load Despatch Centre.

(emphasis supplied)

Based on the above stipulation, a meeting was convened in SLDC on 27.04.2010 wherein all Distribution Licensee were present and authorized SLDC to get it registered with NRLDC on behalf of Discoms and SLDC has been authorized to collect the amount towards NRLDC Charges and disburse the same to NRLDC.  The first bill was raised by NRLDC for the period October 2010 to February 2011 on 23.03.2011.

However, in the meeting held on 05.04.2011 under the Chairmanship of Director (Operations), DTL, it was decided to settle the bills of March 2011 onwards by SLDC Delhi and upto Feb. 2011, the bills are required to be settled by PGCIL / NRLDC directly with Discoms as PGCIL was settling all the bills including NRLDC Charges with Discoms.

The matter was discussed in 20th Commercial Sub-Committee of NRPC meeting held on 24.08.2011 at Jaipur wherein details of credits given by Powergrid to Distribution Companies for the period October 2010 to February 2011 as Powergrid was settling the RLDC Charges till February 2011 to settle the bills for the period October 2010 to February 2011 on the request of NRLDC that these bills may also be settled by SLDC.

The matter was discussed in the 11th meeting of Delhi Commercial Sub-Committee held on 18.10.2010 wherein the issue of the payment for October 2010 to February 2011 was discussed and all Delhi Discoms assured that they would release the charges of NRLDC Fee and Charges for the period October 2010 to February 2011 by 04.11.2011 i.e. 58th day of issue of statement by SLDC on the basis of the receipt of the bill from NRLDC with the intimation of credit of Powergrid to Distribution Companies already done for the period October 2010 to February 2011, received on 07.09.2011 from NRLDC.  Accordingly, payment was collected and disbursed to NRLDC by Delhi SLDC.  Hence, no surcharge is liable to be paid by Delhi SLDC for the payment pertains to the period October 2010 to February 2011.

NRLDC vide letter dated 01.03.2012 included the surcharge for the period October 2010 to March 2011 amounting Rs. 1874231/- along with the bill of February 2012.  However, bills for February 2012 were forwarded to Distribution Companies for payment, copy of which was endorsed to GM, NRLDC stating that the surcharges payment is not acceptable to Delhi SLDC for the period October 2010 to February 2011.

It may also be noted that with regard to NRLDC Charges, SLDC is only a collecting and disbursing agency based on the agreement reached with SLDC and Delhi Discoms and NRLDC.  SLDC can not take any responsibility for non payment of any Discom (s) except reporting the matter to NRLDC and other Regularity Authorities.  NRLDC has to withdraw late payment surcharge bill for the period October 2010 to February 2011 failing which SLDC has no other option but to advise NRLDC to raise the bill directly on Discoms based on the allocation mentioned by SLDC because as per the regulations, SLDC is not bound to act as a Collection and Disbursing agency for these charges.

It may also be noted that the PGCIL is directly raising the bills of Transmission Charges from Discoms in PoC regime also.  In the present regime of NRLDC Charges, Discoms do the TDS on the bills raised by SLDC and thereafter, SLDC also does the TDS for making payment to NRLDC.  Thus, a total 21% TDS is done in this case.  If NRLDC does the collection directly from Discoms, these double deductions of TDS could be foregone.  This was also brought to the notice vide SLDC’s letter dated 24.06.2011 to NRLDC till date no reply has been received.

NRLDC representative opposed the views of SLDC and said that in all the five regions in the country, the respective SLDCs are the nodal agencies for collection and disbursement of RLDC Charges on behalf of the Distribution Licensees.  No special dispensation can be given to Delhi in this regard.

Dy. G.M. (Finance), DTL dealing SLDC finance matters, expressed the Finance Department’s inability to continue to act as Collection and Disbursing Agency as it is creating legal problems in settling the TDS issue apart from the other issues.  He narrated the fact that though payments are received on 58th day or later, the TDS liability starts from the issue of the bill by SLDC.  Further, if any of the Users delays payment, the entire payment of NRLDC gets delayed and attracts Late Payment Surcharge on SLDC. SLDC is only a Collecting and Disbursing Agency and payment liabilities are discharged from a ZERO Balance Account opened in a Nationalized Bank.  It can not discharge the Late Payment Surcharge due to delay in payment by any one of the Users.  He further intimated that due to Bank Holidays or other reasons, some times one or two days payment delay occurs in discharging the payment liabilities to NRLDC by SLDC even though all Users pay the charges.  He requested NRLDC to bill directly on Users on the basis of apportionment of charges fixed by SLDC to avoid all such problems.

NRLDC representative expressed his inability to bill directly to Distribution Licensees / Users.  He gave the details of outstanding dues and surcharge on Delhi Utilities due to delay in payments beyond 60 days.  The details are as under:-

| BILL Month (1) | Date of Bill Issue (2) | Amount in Rs. (3) | Date of Receipt of payment (4) | Name of Party | Amount-Admitted in Rs. (5=6+7+8) | TDS-deducted by users in Rs. (6) |
| --- | --- | --- | --- | --- | --- | --- |
| Jul-11 | 1-Aug-11 | 3698183 | 3-Oct-11 | BRPL, NDPL, NDMC, Bawana | 2725792 | 545160 |
|  |  |  | 11-Nov-11 | BYPL | 972388 | 194478 |
| Aug-11 | 1-Sep-11 | 3698183 | 1-Nov-11 | BRPL, NDPL, NDMC | 2731583 | 535980 |
|  |  |  | 11-Nov-11 | BYPL, Bawana | 966600 | 151979 |
| Sep-11 | 3-Oct-11 | 3678393 | 2-Dec-11 |  | 2566862 | 624526 |
|  |  |  | 12-Dec-11 | BYPL | 967955 | 193591 |
|  |  |  | 21-Dec-11 | NDMC | 143576 | 28716 |
| Oct-11 | 1-Nov-11 | 3678393 | 29-Dec-11 |  | 1123062 | 193602 |
|  |  |  | 4-Jan-12 | BYPL | 1006770 | 232366 |
|  |  |  | 10-Jan-12 | BRPL | 1548562 | 309714 |
| Nov-11 | 1-Dec-11 | 3377010 | 31-Jan-12 | BRPL, NDPL, NDMC, Bawana | 2490637 | 498126 |
|  |  |  | 2-Feb-12 | BYPL | 886372 | 177276 |
| Dec-11 | 2-Jan-12 | 3272023 | 2-Mar-12 |  | 2414273 | 482857 |
|  |  |  | 7-Mar-12 | BYPL | 857750 | 171550 |
| Jan-12 | 1-Feb-12 | 3272023 | 30-Mar-12 |  | 2414273 | 482856 |
|  |  |  | 4-Apr-12 | BYPL | 857750 | 171550 |
| Feb-12 | 1-Mar-12 | 3202471 | 30-Apr-12 |  | 3202472 | 640496 |
| Mar-12 | 2-Apr-12 | 3270838 |  |  |  |  |

| BILL Month (1) | Name of Party | Amount Received (8) | Billed-Admitted (9=3-5) | Delay in Number of days beyond a period of 60 days from date of billing | Rebate/ Surcharge applicable in % | Rebate/ Surcharge applicable in Rs (10) | Net out Standing (11=3-6-8-10) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Jul-11 | BRPL, NDPL, NDMC, Bawana | 2180632 | 2.65 | 3 | -1.25 | -3407 | 20,427 |
|  | BYPL | 777910 |  | 42 | -1.25 | -17017 |  |
| Aug-11 | BRPL, NDPL, NDMC | 2195603 | 0.00 | 1 | -1.25 | -1138 | 5,568 |
|  | BYPL, Bawana | 814621 |  | 11 | -1.25 | -4430 |  |
| Sep-11 |  | 1942336 | 0.30 | - |  |  | 5,170 |
|  | BYPL | 774364 |  | 10 | -1.25 | -4033 |  |
|  | NDMC | 114860 |  | 19 | -1.25 | -1137 |  |
| Oct-11 |  | 929460 | -0.70 | - |  |  | 8,130 |
|  | BYPL | 774404 |  | 4 | -1.25 | -1678 |  |
|  | BRPL | 1238848 |  | 10 | -1.25 | -6452 |  |
| Nov-11 | BRPL, NDPL, NDMC, Bawana | 1992511 | 0.63 | 1 | -1.25 | -1038 | 2,146 |
|  | BYPL | 709096 |  | 3 | -1.25 | -1108 |  |
| Dec-11 |  | 1931416 | 0.00 | - | -1.25 |  | 1,787 |
|  | BYPL | 686200 |  | 5 | -1.25 | -1787 |  |
| Jan-12 |  | 1931417 | 0.00 |  |  |  | 1,072 |
|  | BYPL | 686200 |  | 3 | -1.25 | -1072 |  |
| Feb-12 |  | 2561976 | -0.79 |  |  |  | -1 |
| Mar-12 |  |  |  |  |  |  | 3270838 |
|  |  |  |  |  |  | Total | 3315138 |

He further elaborated that with regard to late payment surcharge imposed for the payment due to from October 2010 to February 2011, PGCIL has already credited the difference into Distribution Companies’ bill during May 2011 though the same was intimated in September 2011.  Distribution Licensees should at least consider the payment dues of NRLDC from the date of adjustment done by PGCIL in this regard.  He further offered that if any Users intend to remit the payment directly with NRLDC, that could be done and he informed that Rajasthan utilities remit directly to NRLDC’s account in spite the accounts are issued to Rajasthan SLDC by NRLDC.

To remit the NRLDC charges directly to NRLDC Charges Accounts when Accounts in this regard are issued by Delhi SLDC, the representatives of Distribution Licensees intimated that in Delhi, it can not be possible as it would create problems for them for auditing of accounts.

After a detailed discussions, NRLDC representative agreed to convince their management to waive off the Late Payment Surcharge as a special case for the period October 2010 to February 2011 and Surcharge imposed to Delhi SLDC due to delay in payment for 2/3 days later than due dates.  He further suggested to take care of advance TDS payment, certain amount may be deducted from the bills due to NRLDC on monthly basis and remit the same in Income Tax Department. He requested to provide the TDS Certificate for claiming the same from Income Tax Department by NRLDC.

Concluding the discussions, GCC advised the following:-

- NRLDC should review the late payment surcharges levied on Delhi SLDC for the payment related to October 2010 to February 2011 and Surcharge imposed to Delhi SLDC due to delay in payment for 2/3 days later than due date.

- All Users should remit the amount in SLDC’s account in respect of NRLDC Charges as per the accounts issued by SLDC by 55th day of the issue of the bill by NRLDC so that SLDC can remit the amount positively by 60th day of the issue of the bill to NRLDC to avoid late payment surcharge.

19	THE STATUS OF INTRASTATE UI POOL ACCOUNT

As per order of DERC dated 31.03.2007, Intrastate ABT has been introduced in Delhi.  SLDC is the Nodal Agency for collection and disbursal of UI amount in Delhi.  As per the Interstate UI Accounts, there is a substantial amount is left as outstanding.  Certain Interstate Utilities are defaulting the UI payment.  The latest position of UI Pool outstanding is as under :-

Position as on 31.03.2012

| Utility | Amount in Rs. Crores outstanding against the utilities for 2011-12 / receivable (+) / payable(-) | Amount outstanding from NRLDC pool account by Delhi as a whole in Rs. Crores for 2011-12 |
| --- | --- | --- |
| IPGCL | 2.53 | 334.36 (receivable) |
| PPCL | 24.81 |  |
| NTPC | 11.79 |  |
| BYPL | 76.00 |  |
| BRPL | (-)54.38 |  |
| TPDDL | 167.70 |  |
| NDMC | 62.65 |  |
| MES | 9.65 |  |
| Total | 300.75 |  |

The pool balance is also being maintained by Delhi SLDC based on time to time decisions of Central and State Regulatory Commissions.  As on 31.03.2012, the pool balance details are as under :-

All figures in Rs. Lacs

| FY | DIFFERENTIAL CAP AMOUNT | ADDITIONAL UI AMOUNT | TOTAL |
| --- | --- | --- | --- |
| 2007-08 | 655 |  | 655 |
| 2008-09 | 1643 |  | 1643 |
| 2009-10 | 292 | 2158 | 2450 |
| 2010-11 | 4582 | 1271 | 5852 |
| 2011-12 | 6404 | 1591 | 7995 |
| TOTAL | 13576 | 5020 | 18595 |

At present against the above pool balance amount, Rs.165 Crores is available due to non payment of full amount by NRPC and BRPL.

The balance in Intrastate UI Account are due to following reasons:-

a) 	From 01.04.2007 to 06.01.2008, the Account was zero balance account i.e. receivable to the account was equal to the payable from the Account.

b)	From 07.01.2008, CERC introduced UI Cap to Generating Stations as per CERC Regulation dated 28.12.2007, Generating Stations UI have been capped 406Ps/kWh when actual exceeds the scheduled generation in case of Generation Stations with Coal and Lignite Firing Stations and Stations burning only APM Gas.

Due to the Cap, the UI Account become non zero balance Account and some amount is left out from the payable and receivable amount by Generators and Discoms.

c)	From 01.04.2009, CERC has come up with comprehensive regulation introducing additional UI Charges on over drawing Discoms under low frequency conditions and under generation stations i.e. frequency below 49.2Hz (40% additional UI Charges at frequency below 49.2Hz.) in addition to the Generation Cap mentioned at point (b) above.

d)	From 03.05.2010, the Additional UI Charges has been as under :-

| Frequency below | Rate |
| --- | --- |
| 49.5Hz. | 40% of additional UI charges at 49.5Hz frequency rate i.e. 873Ps/Unit |
| 49.2Hz. | 100% additional UI Charges at 49.5Hz frequency charges i.e. 100% of 873Ps/Unit |

In addition to this, UI rate is also capped at 403Ps/unit for under drawal in excess of 10% of schedule of 250MW whichever is less.

e)	DERC vide order dated 21.04.2009 and 03.08.2010 implemented the revised UI Regulations adopted by CERC implemented in Delhi.

f)	Due to the above UI Cap imposed on Generators from 07.01.2008 and Additional UI charges imposed on Discoms and Generating Stations from 01.04.2009, the UI receivable becomes less than payable, leaving the balance available funds in UI Pool Account being operated by SLDC.

As on 31.03.2012, about Rs.150 Crores is left as UI Pool balance and the amount is kept as Fixed Deposit for certain term and the accrued interest is also kept in the scheme.

It may also be noted that from 02.04.2012, the UI Regulations have been revised by CERC though stayed by Hon’ble High Court of Madras.

As per the new Regulations, 20% penalty corresponding to the frequency based UI rate for over drawal below frequency 49.7Hz, 40% penalty of maximum of UI rate of Rs.9/Unit for over drawal upto 49.2Hz and 100% penalty at the rate of 900Ps/unit for over drawal below 49.2Hz.

The Cap rate is also fixed at 450Ps/Unit for under drawal in excess of 10% of schedule or 250MW whichever is less.

Generating stations, UI cap rate is 165Ps/unit for injection by generating station except Hydro in access of 105% of the DC in a time block or in access of 101% DC on average on a day.

The cap rate for infirm power injected to the Grid by a unit or a generation station during testing / commissioning prior to CoD of shall be as follows :-

Domestic Coal / Lignite / Hydro		:	Rs. 1.65 / kWh

APM Gas as fuel 				:	Rs. 2.60 / kWh

Imported Coal / RLNG			:	Rs. 3.30 / kWh

Liquid Fuel 					:	Rs. 9.00 /kWh

Decision of utilization of fund is to be taken by DERC.

SLDC has already mooted the proposal for incurring the amount needed for establishing New SLDC from the fund so that the consumers of Delhi won’t be burdened with the cost.

Dy. G. M. (Commercial), NRLDC intimated that there is a huge outstanding dues in respect of UPPCL to the tune of Rs. 1000 Crores and J&K to the tune of Rs. 400 Crores.  CERC has already started the proceedings against the utilities with regard to non payment of UI Charges.  He hoped that with the intervention of the Central Commission, the payment position of UI Pool Account being operated by NRLDC thereby the dues of Delhi utilities would also be got resolved.

GCC noted the position.

20 	Non payment of Energy Bills of IPGCL / PPCL by BYPL and BRPL since October, 2010 (agenda by IPGCL / PPCL).

Since the re-assignment of the PPA signed with DTL, energy is being billed by IPGCL and PPCL to all the Distribution Companies as per the Energy Account issued by the State Load Dispatch Centre, Delhi (SLDC) and the payments for the bills raised were being realized within the stipulated period in the past, as per the PPA/ Regulations issued by the DERC.

The Generating Utilities expressed their inability to continue to the supply of power with the huge liability as they are to pay liabilities to fuel supply agencies (Gas and Coal) to continue the generation.  They also informed that the fuel supply agencies are not allowing any credit facility for such large amount.

However, payments are not being released in full by BRPL and BYPL from the month of October 2010. The details of which are as under:

- Indraprastha Power Generation Company Limited

Summary of outstanding dues as on 03.05-2012                                      (Fig. in Cr.}

| Discom | Outstanding Balance as on 31.03.2011 | Billing since 01.04.2011 | Payment received since 01.04.2011 | Surcharge up to 15.03.2012 | Total |
| --- | --- | --- | --- | --- | --- |
| BRPL | 107.99 | 398.81 | 185.67 | 38.06 | 359.18 |
| BYPL | 66.45 | 266.78 | 89.66 | 26.36 | 269.92 |
| Total | 174.45 | 665.58 | 275.33 | 64.41 | 629.11 |

- Pragati Power Corporation Ltd.

Summary of outstanding dues as on 03.05-2012

| Discom | Outstanding Balance as on 31.03.2011 | Billing since 01.04.2011 | Payment received since 01.04.2011 | Surcharge up to 15.03.2012 | Total |
| --- | --- | --- | --- | --- | --- |
| BRPL | 84.58 | 297.04 | 162.07 | 25.92 | 245.46 |
| BYPL | 63.26 | 199.07 | 79.33 | 20.33 | 203.34 |
| Total | 147.85 | 496.11 | 241.40 | 46.25 | 448.80 |
| Total | 322.29 | 1161.69 | 516.73 | 110.66 | 1077.91 |

Sh. Ajay Kumar, VP, BRPL, explained the reasons of non payment of dues.  He however, assured that the arrear payment would be released as soon as the funds are available through the loans from the banks.  He further clarified that with great difficulties, they are discharging the monthly payment liabilities to utilities.

BYPL representative also expressed the same views.

GCC noted the position and advised the defaulting utilities to pay the dues so that the Generating Utilities can supply power to the consumers un-interruptedly.

21. 	Opening of LC for Bulk Power Supply to BRPL and BYPL by IPGCL and PPCL Power stations (Agenda by IPGCL / PPCL).

IPGCL and PPCL representative informed that various correspondences have been made by IPGCL and PPCL in respect of opening of LC for securing Bulk Power Supply. However, BRPL and BYPL inspite of number of reminders have not established LC in respect of IPGCL and PPCL since April, 2011.

Sh. Ajay Kumar, VP, BRPL explained that due to the exhausting of limits of funds imposed by banks for establishment of LC due to liquidity problem, they are not in a position to establish LC.  LC would be established as and when financial situation of the utility improves.

BYPL representative also expressed the same views.

GCC noted the position and advised the utilities to make all out efforts to establish LC as per the provisions of the PPAs and relevant Regulations of the respective State Electricity Regulatory Commissions.

22	Signing of Supplementary PPA for power supply from the existing stations of IPGCL & PPCL (Agenda by IPGCL / PPCL).

IPGCL / PPCL representative informed that Power Purchase Agreement (PPA) between IPGCL and Delhi Transco Limited (DTL)  executed on 30.03.2007 was re-assigned in favour of DISCOMS by the Delhi Electricity Regulatory Commission (DERC) vide their order dated 31.03.2007. Supplementary PPA has already been signed with TPDDL and NDMC. However, supplementary PPAs are yet to be executed with the BYPL and BRPL. Draft PPA was forwarded to BYPL and BRPL in the 1st week of December 2010.However inspite of number of reminders, BYPL and BRPL have not been signed the agreements without any apparent reasons.

Both BRPL and BYPL representatives informed that the PPA would be executed as early as possible.

23. 	Signing of Power Purchase Agreement for 1371MW Pragati-III Combined Cycle Gas Power Plant at Bawana, Delhi by Military Engineering services (MES) (Agenda by PPCL).

PPCL representative informed that Power Purchase Agreement between Military Engineering Services and PPCL for MES share from 1371MW Pragati-III Combined Cycle Gas Power Plant at Bawana, Delhi has not been executed. Inspite of the repeated follow-ups, an unreasonable delay has been occurring in signing the PPA by MES. The commercial operation of the unit/block of the station has already been commenced.

PPCL representative further intimated that as per the power allocation made by State Government from the project to MES, the power is being scheduled to MES from the date of Commercial Operation of the Unit.

MES representative was not present in the meeting due to which the latest position could not be ascertained.  However, SLDC representative intimated that as per the information provided by the officers visited last week of April 2012 in SLDC intimated that the process for approval of PPA is in advance stage and they hoped the file containing the approval of PPA is expected to be cleared soon.

GCC noted the position.

24	Payment for supply of power from 1371MW Pragati-III Combined Cycle Gas Power Plant, Bawana, Delhi by MES (Agenda by PPCL).

PPCL representative informed that payments are not being made by Military Engineering Services for supply of power from 1371MW Pragati-III Combined Cycle Gas Power Plant. The power from the project has been scheduled to MES by SLDC, Delhi as per the allocation of power made by Govt. of NCT of Delhi. MES has not yet made the payment of Rs. 90, 19,790/- for the invoice raised by PPCL for the energy supplied during the month of December 2011 and January 2012.  MES is also required to pay the applicable surcharge up to date of payment as per the clause no. 35 ‘Late Payment Surcharge’ of CERC (Terms and Conditions of Tariff) Regulations, 2009.

MES representative was not present in the meeting due to which the latest position could not be ascertained.  However, SLDC representative intimated that as per the information provided by the officers visited last week of April 2012 in SLDC intimated that the process for approval of PPA is in advance stage and they hoped the file containing the approval of PPA is expected to be cleared soon.

After getting the approval of PPA, they could release the payment.  It was also cleared that since the power is scheduled to MES from the date of Commercial Operation as per allocation of power from the project to MES they are liable for paying the charges from CoD of the units.

GCC noted the position and reiterated that though the PPA has not been executed with MES by PPCL since power is being availed by MES from Bawana from CoD of the unit, they are liable to pay for purchase of power from CoD of the Units.

Additional Agenda

25	Non-payment of wheeling charges and power purchase liability by BRPL and BYPL since October, 2010 to DTL.

BRPL and BYPL have been defaulting the timely payment of Wheeling Charges bills since October, 2010, the details of outstanding dues as on  01.05.2012  are tabulated below:-

( in  Rupees Crores)

| Nature of payment | BYPL | BRPL |
| --- | --- | --- |
| Wheeling charges | 153.42 | 239.50 |
| Power Purchase Liability | 58.59 | 94.09 |
| Total | 212.01 | 333.59 |

Besides, due to non-payment of above mentioned dues, the LPSC of Rs.56.29 Crores and Rs35.59 Crores as on 31.03.12 is also payable by BRPL and BYPL respectively.

Sh. Ajay Kumar, VP, BRPL, explained the reasons of non payment of dues.  He however, assured that the arrear payment would be released as soon as the funds are available through the loans from the banks.  He further clarified that with great difficulties, they are discharging the monthly payment liabilities to utilities.

BYPL representative also expressed the same views.

GCC noted the position and advised the utilities to chalk out the plants to clear the arrears at the earliest.

26	Non Payment of Incentive bills by BRPL and BYPL to DTL.

G.M (Commercial), DTL informed that the incentive bills for the period 2007-08(Diff.), 2008-09 and 2009-10 was raised to Discoms as per the DERC’s order. BRPL and BYPL have not released payment for incentive bills, the details of which are tabulated as under:

( in Rupees)

| Nature of payment | BYPL | BRPL |
| --- | --- | --- |
| Incentive(2007-08)Diff | 10,09,207 | 12,65,048 |
| Incentive 2008-09 | 48,28,959 | 71,27,943 |
| Incentive 2009-10 | 37,79,909 | 61,31,744 |
| Total | 96,18,075 | 1,45,24,735 |

G.M. (Commercial) further confirmed that TPDDL, NDMC and MES had already released the payment of the aforesaid bills.

GCC noted that the above amount involved is comparatively smaller and requested BRPL and BYPL representatives to clear the payments at the earliest for which the representatives of the utilities agreed to take up the with their management to release the amount as early as possible.

27	Non execution of Connection Agreement by PPCL for Pragati-III(1371 MW CCGT )

General Manager (Commercial), DTL informed that as per the requirement of Delhi Grid Code (DGC), PPCL had submitted a draft connection agreement for Pragati –III (1371 MW CCGT to DTL. After scrutiny of the aforesaid agreement and the related documents, it was observed that some documents/details were not enclosed with the draft connection agreement. Accordingly a letter was issued to GM(Comml.),PPCL on 01.02.2012 followed by reminder dated 02-05-2012 for necessary action, but nothing has been heard so far from PPCL.  He requested PPCL to immediate execute the Connection Agreement.

SLDC representative requested the Chair to intervene the matter as recently CERC has come out heavily on the utilities on the issue of non execution of Connection Agreement with CTU.  It has further directed RLDCs to give the status of Connection Agreement with entered into with Users and CTU as on 31.03.2012.

To avoid consequences of non entering into Connection Agreement, SLDC requested PPCL and DTL to execute the Connection Agreement at the earliest.

GCC advised PPCL and DTL to execute the Connection Agreement for Bawana CCGT by 21.05.2012.

24	HOSTING OF NEXT MEETING OF GCC

The next meeting of GCC would be convened during September 2012.  Exact date & venue of the meeting would be intimated later.

Annexure-1

The list of the officers attended 6th Grid Coordination Committee meeting held on 08.05.2012 at Hotel Connaught, Connaught Place, New Delhi-110001.

| S. No. | Name | Designation | Utility | Mobile no. |
| --- | --- | --- | --- | --- |
| 1 | Sh. A.K. Haldar | Dir (O), Chairperson, GCC | DTL | 9650992550 |
| 2 | Sh. P.K. Ray | Dir(T) | IPGCL | 9818357133 |
| 3 | Sh. V. Venugopal | DGM, SO – Convener GCC | SLDC | 9871093902 |
| 4 | Sh. Bhupender Nath | G.M. (Comml) | DTL | 9999533627 |
| 5 | Sh. Prem Prakash | GM(O&M)-I | DTL | 9999533630 |
| 6 | Sh.R.K. Tola | G.M.(O&M)-II | DTL | 9999533624 |
| 7 | Ms. Kiran Saini | DGM(SCADA) | SLDC | 9540040639 |
| 8 | Sh. P.K. Gupta | DGM(O&M)-II | DTL | 9999533626 |
| 9 | Sh. S.K. Sharma | DGM(M&P) | DTL | 9999533640 |
| 10 | Sh. Loveleen Singh | DGM (OS) | DTL | 9999533659 |
| 11 | Sh.A.C. Agrawal | DGM Plg-I | DTL | 9999533636 |
| 12 | Sh. D.N. Sondhi | Dy. G.M (Fin.) | DTL | 9999533820 |
| 13 | Sh. S.P.Routray | Manager (SS&M) | DTL | 9999533939 |
| 14 | Sh. B.L. Gujjar | Mgr (Prot) | DTL | 9999533985 |
| 15 | Sh.S.S Rao | Mgr (ICM) | DTL | 9999533937 |
| 16 | Sh. S. M. Verma | GM (Project), Gas Station | IPGCL/PPCL | 9717694896 |
| 17 | Sh. Jagdish Kumar | GM Project, Bawana GT | IPGCL/PPCL | 9958701234 |
| 18 | M. Shiva Shunmuganadan | G.M. (Finance) | IPGCL/PPCL | 9910708252 |
| 19 | Sh. Y.P. Arora | GM, GTPS | IPGCL/PPCL | 9717694855 |
| 20 | Sh. R.R. Sinha | GM(HR) | IPGCL/PPCL | 9650822344 |
| 21 | Sh. R.K. Jain | G.M. (Commercial) | IPGCL/PPCL | 9818600955 |
| 22 | Sh. M. Shukla | DGM (Prot.) | IPGCL/PPCL | 9717698228 |
| 23 | Sh. Santosh Kumar | DGM | IPGCL/PPCL | 9717698177 |
| 24 | Sh. Amit Ahuja | DGM (I/C), PPCL | IPGCL/PPCL | 9717079333 |
| 25 | Sh. R.K. Yadav | Manager (Commercial) | IPGCL/PPCL | 9717694845 |
| 26 | Sh. Dinesh Saini | AM(HR) | IPGCL/PPCL | 9717695001 |
| 27 | Sh. R.K. Gupta | AM | IPGCL/PPCL | 9717698293 |
| 28 | Sh. Praveen Kumar | AM(T) | IPGCL/PPCL | 9717694775 |
| 29 | Sh. Sanjay Kr. Sharma | AM(T), Commercial | IPGCL/PPCL | 9717694965 |
| 30 | Sh. P.Devanand | HoG(PS&C) | TPDDL | 9871800506 |
| 31 | Sh. Ashis. Kr. Dutta | AGM (PMG) | TPDDL | 9871798566 |
| 32 | Sh. Sanjay Banga | Sr. G.M.(PSC&A) | TPDDL | 9818108660 |
| 33 | Sh. Ajay Kumar | Vice President | BRPL | 9350683910 |

| S. No. | Name | Designation | Utility | Mobile no. |
| --- | --- | --- | --- | --- |
| 34 | Sh. S. S. Sondhi | AVP (SO) | BRPL | 9312147009 |
| 35 | Sh. Sanjay Srivastav | AVP (PMG) | BRPL | 9312147045 |
| 36 | Sh. Sunil Barnwal | Manager (PMG) | BRPL | 9350261886 |
| 37 | Sh. Mukesh Dadhich | DGM(SO) | BYPL | 9350261451 |
| 38 | Sh. Haridas Maity | Sr. Manager | BYPL | 9350110156 |
| 39 | Sh. Shekhar Saklani | Asstt. Manager | BYPL | 8010618252 |
| 40 | Sh. N.B. Sadasivan | DGM(Comml) | APCPL | 9650990848 |
| 41 | Sh. Sanjay Kumar | Sr, Manager (OS) | APCPL | 9650998955 |
| 42 | Sh. H.K. Chawla | DGM | NRLDC | 9650074803 |
| 43 | Sh. Chaman Lal | SE(E) | NDMC | 9810034499 |
| 44 | Sh. B.K. Yadav | Sr. XEN | BBMB | 9717101444 |
| 45 | Syed K. Alam | Deputy director | DERC | 9999533896 |
| 46 | Sh. S. K. Maheswari | DGM | BTPS | 9650993817 |
| 47 | Sh. Debasis Sen | AGM(O&M) | BTPS | 9650993817 |
| 48 | Sh. A. K. Rathore | Manager (T) | SLDC | 9540040669 |
| 49 | Sh. Ved Prakash | Dy. M. (Finance) | SLDC | 9999533718 |
| 50 | Sh.Sanjeev Kumar | AM, System Operation | SLDC | 9999533917 |
| 51 | Sh. Deepak Sharma | AM, System Operation/EA | SLDC | 9540041008 |
| 52 | Sh. Naveen Kumar | AM(T) | SLDC | 9999533883 |

Annexure-2

MAY-2012

INDEX

S.No.		Chapter		Item					Page No.

1.0		General Principle						3

2.0		Coordination of Protection System				4

2.1		With NRPC						4

2.2		With distribution licensees and Generation		4

3.0		Protection Requirement

3.1		400-220KV lines					4

3.2		400-220,220/66/33KV Power Transformer		4

3.3		Substation Bus Bar Protection				5

3.4		66,33KV Lines						5

3.5		11KV Lines						5

3.6		66/33,66/11 or 33/11Kv Power Transformers	             6

3.7                     Settings Philosophy                                                           7

DELHI TRANSCO LIMITED

In compliance to the provisions contained in Delhi Grid code (DGC) Clause No. 16.3.2 notified by Delhi Electricity Regulatory Commission (DERC) on official Gazette of Delhi on 22.04.2008.  Delhi Transco Ltd. (DTL) being notified as State Transmission Utility in Delhi State makes following Protection Plan for operation of Delhi Power System.

PROTECTION REQUIREMENTS AND CO-ORDINATION

1.0	General Principles

No item of electrical equipment shall be allowed to remain connected to the transmission System unless it is covered by appropriate protection aimed at reliability selectivity, speed, discrimination and sensitivity.  Guidelines mentioned in protection manuals of CBI & P shall be kept in view.

Protection standards are treated as interface issues because of the possible severe cross-boundary repercussions of faults that occur in the system of any entity.  Minimum protection requirements are prescribed in the Section because inadequate protection or mal-operation of protection system of one entity may result in far reaching consequences, disturbances and even damages in the systems of other entities.

All users shall co-operate to ensure correct and appropriate settings of protection to achieve effective, discriminatory removal of faulted equipment.

The protection system to be installed (or kept in service) at various Generating Stations, Grids sub-stations with DTL , S/Stns. with Distribution Licensees shall not be inferior to already in vogue.  The stakeholders shall update the protection system as technology advances worldwide.

Protection settings shall not be altered without consulting and informing all affected users.  No protection should be by-passed or disconnected without the agreement of the affected user.  When protection is by passed and/or disconnected by agreement then the cause must be rectified and the protection restored to normal condition as quickly as possible.  If agreement has not been reached the electrical equipment shall be removed from service forthwith.  Even when protection is temporarily by passed by agreement, a standby protection or back-up protection system shall be operational during the period.

DTL shall have two functions to perform in respect to protection of power system in Delhi.

- Protection coordination with Northern Region Power System that is coordination of relays in 400/220KV system including interstate line.  This system is monitored by NRPC Protection system committee.

- Co-ordination of protection system at DISCOM’s and GENCO connected to DTL EHV sub-station in the following manner.

2.0  	Co-ordination of Protection system

2.1	With NRPC

Far end any third party, each end will set its relay as per general practice of relay setting and the protection on either end shall be mutually agreed and setting provided.  A set of relay coordination setting shall be forwarded to NRPC for their study, reference and record.  Any setting change as proposed by NRPC protection committee shall be implemented after due consideration.

2.2	With Distribution Licensees and Generation

When new equipment (including generating units) and lines are planned to be constructed the proposed protections and settings (which shall be in accordance with standards in vogue) shall be communicated to STU.  The protection systems shall be installed as per provisions of new connection or modification by users after concurrence of STU.  Commissioning of new equipment/lines may necessitate modifications of existing protections or revision of relay settings coordinated in consultation with DTL as STU.

3.0	Protection Requirements

3.1	400-220KV Lines:

Main-I  protection shall be IEC 61850  compliant communicable  Numerical Distance Protection with minimum three zones with  built in fault locator,   Disturbance Recorder & Event loggers.  Main-II Protection shall be again IEC 61850 Compliant Numerical Distance Protection or61850 compliant Numerical Line Current Differential.

Necessary indications, alarms and controls shall be provided for Line CVT supply failure and for ensuring change over to Bus No.I PT to Bus No.2 PT and vice versa when Bus transfer is made.

Norms for Protection of 400/220KV Lines

| S.No. | Voltage | Protection scheme |
| --- | --- | --- |
| 1. | 400KV Lines | Main.I & 2 will be numerical communicable IEC 61850 compliant distance protection scheme with built in Fault Locator. Disturbance Recorder and Event loggers of scheme as per nation policy or Main-2 numerical line current differential with IEC 61850 compliant. |
| 2. | 220KV Lines | Main-1 & 2 will be numerical communicable IEC 61850 compliance distance protection scheme with built in Fault Locator, Disturbance Recorder and Event Loggers of scheme as per nation policy or Main-2 numerical line current differential with IEC 61850 compliant. |

3.2	400/220 and 220/66/33KV Power Transformers

All windings of power transformers of EHT class shall be protected by differential relays, REF relay for HV & LV winding.  Two separate relays to be provided for Main Protection e.g differential and REF and Back up relay should be separate.  Over-fluxing relays shall be provided for EHT transformers.  In addition there shall be back up time lag over current and earth fault protection.  For parallel operation such as back up protection shall have a directional feature.  For protection against heavy short circuits, the over current relays should be incorporate with a high set instantaneous element.  In addition to electrical protection, gas operated relays sudden pressure/PRV winding temperature protection and oil temperature protection shall be provided.

Norms for Protection of 400/22O, 220/66-33KV Power Transformers

| Voltage ratio and capacity | HV side | LV Side | Common relays |
| --- | --- | --- | --- |
| 400/220KV | Directional 2 o/c and 1 directional E/F relay, REF. | Directional 2 O/C and 1 directional E/F relay, REF | Numerical differential relay and separate REF’s over load. Overflux Buchloz OLTC Bucholz, PRV, OT, WT, SPR |
| 220/66-33/11 KV | 2 o/c and 1 E/F relay REF | 2 O/C and 1 E/F relay, REF | Numerical differential relay and separate REF’s. Over flux, Buxhloz OLTC Buchloz, PRV, OT WT, SPR. |

3.3 	Substation Bus Bar Protection

Adequate bus bar protection for each busbar zone in the substation for all 400/220KV class substations shall be provided.

3.4	66/33kv Lines

Main.I shall be Numerical three zone distance or line current differential protection scheme.  The back up directional over current & directional earth fault or non directional over current and earth fault with high set as per the line requirement.  Necessary indications alarms and control shall be provided on failure of PT supply.

3.5	11KV Lines

The 11KV/6.6KV distribution S/Stn. fed from GENCO/TRANCO/DISCOM S/Stn. shall also be provided with following suitable protection:

1. Non directional over current and earth fault with high set.

2. Time lag fuse/MCB protection

Protection norms for 66KV, 33KV & 11KV feeders

| Line | Protection as per agenda | Protection after amendment |
| --- | --- | --- |
| 66KV line in mesh | Main-I Distance/line current differential protection & directional O/C and E/F with high set. | Main Protection:- IEC61850 compliant Numerical Distance Protection/line current differential protection with built in fault locator , disturbance recorder and event logger for all overhead lines of length more than 1 KM. For all underground cables and over head lines upto 1 km. length main protection shall be essentially Numerical line current differential protection. Back up Protection:- Directional Over Current and Earth Fault protection. |
| 66KV double ckt. parallel fdr. | Main.I Distance/line current differential protection and directional O/C & E/F. | Main Protection:- IEC61850 compliant Numerical Distance Protection/line current differential protection with built in fault locator , disturbance recorder and event logger for all overhead lines of length more than 1 KM. For all underground cables and over head lines upto 1 km. length main protection shall be essentially Numerical line current differential protection. Back up Protection:- Directional Over Current and Earth Fault protection. |
| 33KV Parallel feeder | Distance/line current differential protection & directional O/C & E/F. | Main Protection:- IEC61850 compliant Numerical Distance Protection/line current differential protection with built in fault locator , disturbance recorder and event logger for all overhead lines of length more than 1 KM. For all underground cables and over head lines upto 1 km. length main protection shall be essentially Numerical line current differential protection. Back up Protection:- Directional Over Current and Earth Fault protection. |
| 66KV single ckt. feeder | Distance/line current differential protection. Non direction O/C E/F. | Main Protection:- IEC61850 compliant Numerical Distance Protection/line current differential protection with built in fault locator , disturbance recorder and event logger for all overhead lines of length more than 1 KM. For all underground cables and over head lines upto 1 km. length main protection shall be essentially Numerical line current differential protection. Back up Protection:- Non Directional Over Current and Earth Fault protection. |
| 33KV single ckt. feeder | Distance/line current differential protection. Non direction O/C E/F. | Main Protection:- IEC61850 compliant Numerical Distance Protection/line current differential protection with built in fault locator , disturbance recorder and event logger for all overhead lines of length more than 1 KM. For all underground cables and over head lines upto 1 km. length main protection shall be essentially Numerical line current differential protection. Back up Protection:- Non Directional Over Current and Earth Fault protection. |
| 11KV feeder emanating from DTL/GENCO Grid (with minimum settings) | Non-directional O/C E/F with high set feature. | Non-directional O/C E/F with high set feature (at first switching station control shall be with CB only). |

3.6	66/33, 66/11KV or 33/11KV Power Transformers

The following shall be norms of protection for transformers on different voltage classes and capacity ratings:

Norm for Protection for EHV Class Power Transformers

| Voltage ratio and capacity | HV Side | LV Side | Common relays |
| --- | --- | --- | --- |
| 66/33KV | 2 O/C and 1 E/F relay, REF | 2 O/C and 1 E/F relay, REF | Differential Buchloz, OLTC B |
| 66/11KV | 2 O/C and 1 E/F relay, REF | 2 O/C and 1 E/F relay REF | Differential Buchloz, OLTC Buchloz, PRV, OT, WT. |
| 33/11KV | 2 O/C and 1 E/F relay | 2 O/C and 1 E/F relay | Differential Buchloz, OLTC Buchloz, PRV, OT WT. |

3.7      Settings Philosophy

| S.No. | Protection setting | Reach & Time |
| --- | --- | --- |
| 1. | Long lines Zone.I | 80% of the Protection line, instantaneous. |
|  | Zone.2 | 100% of the Protection line + 50% of the shortest line emanating from the far end bus bar or 120% of the Protected line whichever is higher. Time setting 350ms for short lines(<100 kms and 500ms for line lines > 100 km |
|  | Zone-3 | 120% of the Protected line + 100% of the shortest line emanating from the far end bus bar or 100% of the Protected line + 100% of the longest line emanating from the far end bus bar + 25% of the longest line emanating from the far end of the second line considered which ever is lower. The zone setting to be limited such that it will not reach into the next voltage level. Time setting : 1000m sec. |
|  | Zone 3 R/Reverse Zone | 25% of Zone-I reach Time setting : 1000 m sec. |
| 2. | Line with series and other compensations in the vicinity of substations. | 80% of the protected line. 100ms time delay for allowing correct distance measurement after the series capacitor is bypassed. |
| 3. | Power Swing Blocking | Block tripping in all zones, all times. Out of step tripping to be applied on all inter regional tie lines. Deblock time delay = 2s. |
| 4. | Protection for broken conductor | Negative sequence current to positive Sequence current ration more than 0.2 (12/11> = 0.2) only for alarm : time delay = 3.5 Sec. |
| 5. | Carrier Protection | To be applied on all 400KV and 220KV lines with the only exception of radial feeders. |
| 6. | Back up Protection | 1) on 400 & 220KV Lines with 2 Main Protections, back up Earth Fault protection alone to be provided. No over current protection to be applied. 2) On 220KV and lower voltage lines with only one Main Protection Back up Protection by IDMT O/C and E/F to be applied. |
| 7. | Auto Re closing with dead time | Single pole trip and re-closing Dead time = 1.0s. Reclaim time = 25.0s |
| 8. | LBB Protection and bus bar protection | To be applied on all 400KV Sub-stations with the only exception of 220KV radial fed bus bar. LBB current sensor 1>20% in LBB time delay = 200 ms |

Annexure-3

EXTRACTS OF CPRI REPORT OF PROTECTION AUDIT INDICATING FAULT LEVEL COMPUTATION AT DIFFERENT 220KV S/STNS.

APPENDIX 1E(B); SINGLE BUS BAR REPRESENTATION TWO LEVEL CONTRIBUTION TO 
1Ø TO GROUND FAULT AT DIFFERENT 220kV BUSES OF DTL

| SINGLE BUS BAR REPRESENTATION TWO LEVEL CONTRIBUTION TO 1Ø TO GROUND FAULT AT DIFFERENT 220kV BUSES OF DTL |
| --- |
| Sl.no | Fault at BUS | Contributions to the Fault (kA) |  |
|  |  | First level | Second level |  |
|  |  | Element | Contribution (3I0) | Element | Contribution (3I0) | Iphase |
| 1 | Badarpur 220kV 23.94kA 96.7deg | Equivalent Source | 15.741 kA -86.3 deg |  |  |  |
|  | Ballabgarh-1 | 2.244 kA -80.3 deg | Equivalent Source | 4.498kA -90.0deg | 5.469 KA |
|  | Ballabgarh-2 | 2.244 kA -80.3 deg |  |  |  |
|  | Okhla-1 | 0.192 kA 93.5 deg | Tr 1 220/66 | 0.068 kA -269.999 deg | 0.231 KA |
|  |  |  | Tr 2 220/66 | 0.068 kA-269.999 deg | 0.231 KA |
|  |  |  | Tr 1 220/33 | 0.055 kA-269.998 deg | 0.089 KA |
|  | Okhla-2 | 0.165 kA 93.6 deg | Tr 2 220/33 | 0.055 kA-269.998 deg | 0.077 KA |
|  |  |  | Tr 3 220/33 | 0.054 kA-269.998 deg | 0.234 KA |
|  |  |  | Tr 4 220/33 | 0.054 kA-269.998 deg | 0.240 KA |
|  | MehrauliA-1 | 2.187 kA -76.1 deg | Mehrauli2B | 4.728 kA-98.356 deg | 8.004 KA |
|  | MehrauliA-2 | 2.187 kA -76.1 deg | Tr 1 220/66 | 0.117 kA-269.999 deg | 0.250 KA |
|  |  |  | Tr 2 220/66 | 0.117 kA-269.999 deg | 0.289 KA |
|  |  |  | Tr 3 220/66 | 0.117 kA-269.999 deg | 0.247 KA |
|  | NOIDA2 | 0.252 kA 89.9 deg | Gazipur 1 | 0.243 kA -269.90 deg | 0.577 KA |
|  |  |  | synch Gen | 0.011 kA -179.99 deg | 0.540 KA |
| 2 | Maharani Bagh 220kV 8.949kA 99.0deg | Pragathi2A | 0.432 kA 93.4 deg | ParkstretA | 0.243 kA -269.983 deg | 0.394 KA |
|  |  |  | ParkstretB | 0.243 kA -269.982 deg | 0.397 KA |
|  |  |  | S.vihar2A | 0.054 kA -89.962 deg | 0.203 KA |
|  | S.vihar2A | 0.099 kA 93.4 deg |  |  |  |
|  |  |  | Pragathi2A | 0.058 kA -269.917 deg | 0.203 KA |
|  |  |  | Tr1 220/66 | 0.019 kA -269.994 deg | 0.206 KA |
|  | Lodi road 2A-1 | 0.249 kA 93.5 deg | Tr 1 220/33 | 0.249 kA -269.999 deg | 0.288 KA |
|  | Lodi road 2B-2 | 0.249 kA 93.5 deg | Tr 2 220/33 | 0.249 kA -269.999 deg | 0.304 KA |
|  | Tr 1 400/220 | 4.989 kA-81.6 deg | DADRI4 | 2.913 kA 260.308 deg | 2.412 KA |
|  | Tr 2 400/220 | 4.989 kA-81.6 deg | Ballabgarh4 | 2.574 kA 260.380 deg | 2.123 KA |

| Sl.no | Fault at BUS | Contributions to the Fault (kA) |  |
| --- | --- | --- | --- |
|  |  | First level | Second level |  |
|  |  | Element | Contribution (3I0) | Element | Contribution (3I0) | Iphase |
| 3 | IP station 220kV 10.122kA 95.8deg | pragathi2B-1 | 0.000 kA -86.6 deg |  |  |  |
|  | pragathi2B-2 | 0.000 kA -86.6 deg |  |  |  |
|  | Patparganj2A-1 | 5.196 kA -84.4 deg | Gita colony 2A | 5.562 kA 262.076 deg | 4.480 KA |
|  |  |  | Patparganj33A Tr-1 | 0.121 kA 90.001 deg | 0.195 KA |
|  |  |  | Patparganj331 Tr-2 | 0.172 kA 90.001 deg | 0.146 KA |
|  |  |  | Patparganj33B Tr-4 | 0.121 kA 90.001 deg | 0.196 KA |
|  |  |  | Patparganj 2B | 0.044 kA 270.001 deg | 0.106 KA |
|  | Patparganj2B-2 | 5.196 kA -84.4 deg | Gita colony 2B | 5.562 kA 262.076 deg | 4.480 KA |
|  |  |  | Patparganj66A Tr1 | 0.163 kA 90.001 deg | 0.190 KA |
|  |  |  | Patparganj66B Tr2 | 0.163 kA 90.001 deg | 0.191 KA |
|  |  |  | Patparganj 2A | 0.044 kA 90.001 deg | 0.106 KA |
|  | IPStation 33 Tr-1 | 0.09 kA 86.6 deg | shunt | 1.775kA 90.0 deg | 1.348 KA |
|  | IPStation 33 Tr-2 | 0.09 kA 86.6 deg |  |  |  |
|  | IPStation 33 Tr-3 | 0.09 kA 86.6 deg |  |  |  |
| 4 | At Patparganj 220kV(A) 11.037kA 95.7deg | Ipstation 2-1 | 0.132 kA 86.8 deg | Pragthi2B-1 | 0.001 kA 90.000 deg | 0.548 KA |
|  |  |  | Pragthi2B-2 | 0.001 kA 90.000 deg | 0.548 KA |
|  |  |  | Patparganj2B-2 | 0.133 kA 269.828 deg | 0.582 KA |
|  |  |  | IPStation 220/33 Tr1 | 0.087 kA 90.002 deg | 0.212 KA |
|  |  |  | IPStation 220/33 Tr2 | 0.087 kA 90.002 deg | 0.212 KA |
|  |  |  | IPStation 220/33 Tr3 | 0.087 kA 90.002 deg | 0.212 KA |
|  | Gita colony 2A-1 | 6.048 kA -84.1 deg | South of wazirabad 2A | 6.086 kA 262.915 deg | 4.995 KA |
|  |  |  | Gita colony Tr 220/33A-1 | 0.037 kA 90.003 deg | 0.094 KA |
|  | patparganj2B | 5.562 kA -84.5 deg | Ipstation 2 - 2 | 0.134 kA 89.864 deg | 0.582 KA |
|  |  |  | Gita colony 2B - 2 | 6.046 kA 262.078 deg | 4.944 KA |
|  | Patparganj33A Tr-1 | 0.132 kA 87.0 deg | shunt | 0.876 kA 90.000 deg | 0.678 KA |
|  | Patparganj33 1 Tr-2 | 0.186 kA 87.0 deg | shunt | 1.248 kA 90.000 deg | 0.952 KA |
|  | Patparganj33B Tr-4 | 0.132 kA 87.0 deg | shunt | 0.876 kA 90.000 deg | 0.676 KA |

| Sl.no | Fault at BUS | Contributions to the Fault (kA) |  |
| --- | --- | --- | --- |
|  |  | First level | Second level |  |
|  |  | Element | Contribution (3I0) | Element | Contribution (3I0) | Iphase |
|  | At Patparganj 220kV(B) 11.037kA 95.7deg | Ipstation 2 - 2 | 0.132 kA 86.8 deg | Pragthi2B-1 | 0.001 kA 90.037 deg | 0.548 KA |
|  |  |  | Pragthi2B-2 | 0.001 kA 90.037 deg | 0.548 KA |
|  |  |  | Patparganj2A-1 | 0.133 kA 269.828 deg | 0.582 KA |
|  |  |  | IPStation 220/33 Tr1 | 0.087 kA 90.002 deg | 0.212 KA |
|  |  |  | IPStation 220/33 Tr2 | 0.087 kA 90.002 deg | 0.212 KA |
|  |  |  | IPStation 220/33 Tr3 | 0.087 kA 90.002 deg | 0.212 KA |
|  | Gita colony 2B | 6.048 kA -85.1 deg | South of wazirabad 2B-2 | 6.086 kA 262.915 deg | 4.995 KA |
|  |  |  | Gita colony Tr 220/33B-2 | 0.037 kA 90.003 deg | 0.187 KA |
|  | Patparganj2A | 5.469 kA -84.2 deg | Ipstation 2 | 0.134 kA 89.864 deg | 0.582 KA |
|  |  |  | Gita colony 2A | 6.046 kA 262.078 deg | 4.494 KA |
|  | Patparganj66A | 0.177 kA 87.0 deg | Shunt | 0.591 kA 90.000 deg | 4.458 KA |
|  | Patparganj66B | 0.177 kA 87.0 deg | Shunt | 0.591 kA 90.000 deg | 4.458 KA |
| 5 | At Geetha colony 220kV(A) 12.402 kA 95.4deg | Patparganj2A-1 | 0.519 kA 87.5 deg | IPsation2-1 | 0.129 kA 90.038 deg | 0.605 KA |
|  |  |  | Patparganj33A-1TR | 0.127 kA 90.001 deg | 0.195 KA |
|  |  |  | Patparganj33A-2TR | 0.181 kA 90.001 deg | 0.146 KA |
|  |  |  | Patparganj33A-4TR | 0.127 kA 90.001 deg | 0.197 KA |
|  | South of wazirabad 2A-1 | 6.759 kA-85.3 deg | Mandola2-2 | 3.370 kA 264.530 deg | 2.780 KA |
|  |  |  | Mandola2-3 | 3.572 kA 264.530 deg | 2.946 KA |
|  |  |  | Kasmirgate2A-1 | 0.051 kA 90.028 deg | 0.071 KA |
|  |  |  | Kasmirgate2B-2 | 0.051 kA 90.028 deg | 0.071 KA |
|  |  |  | South of wazirabad 66A-Tr1 | 0.135 kA 90.001 deg | 0.228 KA |
|  | Gitacolony 2B | 6.198 kA-84.8 deg | Patparganj 2B | 0.521 kA 90.127 deg | 0.881 KA |
|  |  |  | South of wazirabad 2B | 6.756 kA 262.916 deg | 5.649 KA |
|  |  |  | Tr.33kV-2 | 0.041 kA 90.003 deg | 0.187 KA |
|  | GITA Tr 220/33A-1 | 0.042 kA 87.7 deg | Shunt | 0.273 kA 90.000 deg | 0.214 KA |

| Sl.no | Fault at BUS | Contributions to the Fault (kA) |  |
| --- | --- | --- | --- |
|  |  | First level | Second level |  |
|  |  | Element | Contribution (3I0) | Element | Contribution (3I0) | Iphase |
|  | At Geetha colony 220kV(B) 12.402 kA 95.4deg | Patparganj2B-2 | 0.519 kA 87.5 deg | IPsation2-2 | 0.129 kA 90.038 deg | 0.605 KA |
|  |  |  | Patparganj220/66 Tr 1 | 0.172 kA 90.001 deg | 0.190 KA |
|  |  |  | Patparganj220/66 Tr 2 | 0.172 kA 90.001 deg | 0.191 KA |
|  | South of wazirabad 2B-2 | 6.759 kA -85.2 deg | Mandola2-1 | 3.370 kA 264.530 deg | 2.780 KA |
|  |  |  | Mandola2-4 | 3.572 kA 264.530 deg | 2.946 KA |
|  | Gitacolony 2A | 6.198 kA-84.6 deg | Patparganj 2A | 0.521 kA 90.126 deg | 0.881 KA |
|  |  |  | South of wazirabad 2A | 6.756 kA 262.916 deg | 5.649 KA |
|  |  |  | Tr.33kV-1 | 0.041 kA 90.003 deg | 0.095 KA |
|  | GITA Tr 220/33B-2 | 0.042 kA 87.7 deg | Shunt | 0.273 kA 90.000 deg | 0.211 KA |
| 6 | IP Ext. (Pragthi 2A) 7.947 kA 99.8deg | MaharaniBagh 2-1 | 7.224 kA - 80.6 deg | S.Vihar 2A-1 | 1.271 kA -275.053 deg | 1.065 KA |
|  |  |  | Lodi Road 2A-1 | 0.224 kA -269.921 deg | 0.289 KA |
|  |  |  | Lodi Road 2B-2 | 0.224 kA -269.921 deg | 0.289 KA |
|  |  |  | Tr-1MaharaniBagh 4 | 4.471 kA -94.881 deg | 3.602 KA |
|  |  |  | Tr-2 MaharaniBagh 4 | 4.471 kA -94.881 deg | 3.602 KA |
|  | Park street-1 | 0.252 kA 93.1 deg | Tr-1 220/33 | 0.126 kA -269.999 deg | 0.170 KA |
|  |  |  | Tr-2 220/33 | 0.127 kA -269.999 deg | 0.171 KA |
|  | Park street-2 | 0.252 kA 93.1 deg | Tr-1 220/66 | 0.125 kA -262.999 deg | 0.226 KA |
|  |  |  | Tr-2 220/66 | 0.128 kA -269.999 deg | 0.232 KA |
|  | IP Ext.(Pragthi 2B) 9.351 kA 95.9 deg | IPstation2-1 | 4.677 kA -84.1 deg | Patparganj 2A | 4.799 kA 261.057 deg | 4.122 KA |
|  | IPstation2-2 | 4.677 kA -84.1 deg | Patparganj 2B | 4.799 kA 261.057 deg | 4.122 KA |
|  |  |  | IPS 220/33 Tr -1 | 0.082 kA 90.002 deg | 0.212 KA |
|  |  |  | IPS 220/33 Tr -2 | 0.082 kA 90.002 deg | 0.212 KA |
|  |  |  | IPS 220/33 Tr -3 | 0.082 kA 90.002 deg | 0.212 KA |

| Sl.no | Fault at BUS | Contributions to the Fault (kA) |  |
| --- | --- | --- | --- |
|  |  | First level | Second level |  |
|  |  | Element | Contribution (3I0) | Element | Contribution (3I0) | Iphase |
| 7 | At Saritha vihar 220kV(A) 7.101 kA 99.8deg | MaharaniBagh2-1 | 4.476 kA -80.6 deg | Pragthi2A | 3.085 kA -274.775 deg | 2.111 KA |
|  |  |  | Lodiroad2A | 0.200 kA -269.921 deg | 0.281 KA |
|  |  |  | Lodiroad2B | 0.200 kA -269.921 deg | 0.281 KA |
|  |  |  | Tr 400/220 - 1 | 3.980 kA -94.881 deg | 3.247 KA |
|  |  |  | Tr 400/220 - 2 | 3.980 kA -94.881 deg | 3.247 KA |
|  | Pragthi2A-1 | 2.667 kA -80.3 deg | MaharaniBagh2 | 3.084 kA -95.396 deg | 2.111 KA |
|  |  |  | Parkstreet A -1 | 0.208 kA -269.983 deg | 0.385 KA |
|  |  |  | Parkstreet B -2 | 0.208 kA -269.983 deg | 0.385 KA |
|  | SVIHR66A Tr-2 | 0.021 kA 92.3deg | Shunt | 0.067 kA -270.000 deg | 0.055 KA |
| 8 | At SOW 220kV(A) 14.694 kA 94.9 deg | Mandola 2-2 | 3.927 kA -86.7 deg | Gopalpur B-1 | 0.136 kA -269.634 deg | 0.424 KA |
|  | Mandola 2-3 | 4.164 kA -85.7 deg | Gopalpur A-2 | 0.136 kA -269.634 deg | 0.424 KA |
|  |  |  | South of Wazirabad 2B-1 | 3.930 kA-271.425 deg | 3.312 KA |
|  |  |  | South of Wazirabad 2B-4 | 4.165 kA -271.425 deg | 3.511 KA |
|  |  |  | Narela 2DB-1 | 0.219 kA -269.525 deg | 0.417 KA |
|  |  |  | Narela 2DB-2 | 0.219 kA -269.525 deg | 0.417 KA |
|  |  |  | Mandola Tr 400/220 -1 | 4.225 kA -91.347 deg | 3.488 KA |
|  |  |  | Mandola Tr 400/220 -2 | 4.225 kA -91.347 deg | 3.448 KA |
|  |  |  | Mandola Tr 400/220 -3 | 4.225 kA -91.347 deg | 3.448 KA |
|  |  |  | Mandola Tr 400/220 -4 | 4.225 kA -91.347 deg | 3.448 KA |
|  | Kashmir gate 2A 1 | 0.06 kA 88.8 deg | Tr.33A - 1 | 0.058 kA 90.002 deg | 0.054 KA |
|  | Kashmir gate 2B 2 | 0.06 kA 88.8 deg | Tr.33B - 2 | 0.058 kA 90.002 deg | 0.091 KA |
|  | GITA2A-1 | 0.531 kA 88.5 deg | Patparganj 2A - 1 | 0.491 kA 90.169 deg | 0.888 KA |
|  |  |  | GITA Tr -1-220/33A | 0.039 kA 90.003 deg | 0.094 KA |
|  | SOW2B | 7.404 kA -85.1 deg | Mandola2-1 | 3.926 kA 264.531 deg | 3.314 KA |
|  |  |  | Mandola2-4 | 4.161 kA 264.531 deg | 3.512 KA |
|  |  |  | GITA2B | 0.533 kA 90.342 deg | 0.998 KA |
|  |  |  | Tr.66 - 2 | 0.077 kA 90.002 deg | 0.178 KA |
|  |  |  | Tr.66 - 3 | 0.077 kA 90.002 deg | 0.178 KA |
|  | SOW 220/66A -Tr1 | 0.159 kA 88.9 deg | shunt | 0.526 kA 90.000 deg | 0.433 KA |

| Sl.no | Fault at BUS | Contributions to the Fault (kA) |  |
| --- | --- | --- | --- |
|  |  | First level | Second level |  |
|  |  | Element | Contribution (3I0) | Element | Contribution (3I0) | Iphase |
|  | At SOW 220kV(B) 14.694 kA 94.9deg | MANDL2 - 1 | 3.927 kA -85.7 deg | Gopalpur B-1 | 0.136 kA -269.634 deg | 0.424 KA |
|  | MANDL2 - 4 | 4.164 kA -85.7 deg | Gopalpur A-2 | 0.136 kA -269.634 deg | 0.424 KA |
|  |  |  | South of Wazirabad 2A-2 | 3.930 kA-271.425 deg | 3.511 KA |
|  |  |  | South of Wazirabad 2A-3 | 4.165 kA -271.425 deg | 3.511 KA |
|  |  |  | Narela 2DB-1 | 0.219 kA -269.525 deg | 0.417 KA |
|  |  |  | Narela 2DB-2 | 0.219 kA -269.525 deg | 0.417 KA |
|  |  |  | Mandola Tr 400/220 -1 | 4.225 kA -91.347 deg | 3.448 KA |
|  |  |  | Mandola Tr 400/220 -2 | 4.225 kA -91.347 deg | 3.448 KA |
|  |  |  | Mandola Tr 400/220 -3 | 4.225 kA -91.347 deg | 3.448 KA |
|  |  |  | Mandola Tr 400/220 -4 | 4.225 kA -91.347 deg | 3.448 KA |
|  | GITA2B- 2 | 0.531 kA 88.5 deg | PTPNG2B - 2 | 0.491 kA 90.169 deg | 0.888 KA |
|  |  |  | Gita colony Tr -2 - 220/33B | 0.039 kA 90.003deg | 0.186 KA |
|  | SOW2A | 7.284 kA -85.0 deg | Mandola2-2 | 3.926 kA 264.531 deg | 3.314 KA |
|  |  |  | Mandola2-3 | 4.161 kA 264.531 deg | 3.512 KA |
|  |  |  | Gita colony 2A | 0.533 kA 90.342 deg | 0.998 KA |
|  |  |  | K gate 2A 1 | 0.059 kA 90.029 deg | 0.073 KA |
|  |  |  | K gate 2B 2 | 0.059 kA 90.029 deg | 0.073 KA |
|  |  |  | Tr. 66 - 1 | 0.158 kA 90.001 deg | 0.234 KA |
|  | SOW Tr-2-220/66B | 0.078 kA 88.9 deg | shunt | 0.512 kA 90.000 deg | 0.421 KA |
|  | SOW Tr-3-220/66B | 0.078 kA 88.9 deg |  |  |  |

******

Annexure-4

DELHI TRANSCO LIMITED

METERING PROCEDURE

MAY-2012

##### Index

S.No. 	Chapter 		Item							Page No.

1.	Short titles, extent and commencement						05

2	Definitions 										05

3	Introduction 										06

3.1	The Interface ABT Metering 			07

3.1.1	Operational Metering				07

3.2	Objective						07

4.	Specification and accuracy limits for the

meters and associated equipment. 						07

4.1 	Functional requirement for ABT meters		07

4.1.1    Instrument Transformers				09

4.1.2    Overall Accuracy of Equipments			09

4.2   	 Functional Requirements for Audit and

Accounting meters				            09

4.3	Standards						10

5.	Location and installation of meters						10

  - Installation 						12

  - Following Responsibility				12

  - Metering between DTL and other licensees	12

  - Notice of installation of new meters		13

6.	Procedure to ensure conformance to the accuracy limits,

testing and replacement of meters.						13

  - Procedure and periodicity				13

  - Procedure associated with maintenance of

the meters proper functioning			14

  - Inspection and Testing of meters 			14

6.3.1	Testing of Main and Check meters		14

6.3.2	Accuracy / check and Test Performa’s 		14

6.3.3	Defective meter replacement			14

6.4	Safety of Meters					14

6.5	Sealing of Meters					15

6.5.1	Sealing arrangement				15

6.5.2	Removal of Seals from meters			15

6.5.3	Inspection of Meters					15

7.	Provisions related to right of access to the meters.				16

  - Right of access					16

S.No. 	Chapter 		Item						 Page No.

  - Access with equipment				16

  - Authorization for access				16

  - Limiting Disruption and Disturbances		16

  - Safety procedures					16

  - Responsibilities of Access				16

8. 	Rights, responsibilities and procedures related to recording, collection,

transfer, processing and storage of data collected from meters.		17

  - Rights							17

  - Responsibilities and procedures			17

related to recording, collection,

transfer, processing and storage

of data collected from meters

9.	Provisions related to ownership of metering data.			 		17

10.	Procedure to address metering discrepancies, defective

equipment and meter failure.								17

10.1 	To address metering discrepancies.			17

10.2 	Defective equipment.					18

10.3	Meter failure						18

10.3.1	Assumed meter readings in the event

of faulty metering					18

10.3.2	Non Functioning of Meter				18

10.3.3	Other cases of inaccuracy	and resolution 		18

10.3.4  Voltage Transformer Fusing 				19

11	Procedure for resolution of disputes on metering:					19

11.1	Disputes						19

11.1.1	General						19

11.1.2	Referrals to the Metering Committee			19

11.2      Metering committee					20

11.2.1  Composition of Metering Committee			20

11.2.2   Communicating Revisions to the

Metering Code					20

11.3   	Information						20

11.3.1	Provision of information to DTL.			20

11.3.2	Dispute Resolution.					20

11.4 	Ownership of Metering Data.				20

11.5	Settlement of Disputes				20

S.No. 	Chapter 		Item						    	Page No.

12.	Others											21

12.1	Amendments to the Performa’s			21

12.2	Provision of information to DTL.			21

12.3	Dispute Resolution					21

12.4	List of Intrastate ABT meters.			21

13    Operational metering									21

13.1      Scope							21

13.2      Standards						22

13.3      Operating Characteristics				22

13.4      Metering Components				22

13.4.1	 Energy Meter 					22

13.4.2	 Current Transformers					22

13.4.3	 Voltage Transformers				22

13.4.4	 Power Supplies 					22

13.5      Overall Accuracy of Equipment			23

13.5.1	 Accuracy of time keeping 				23

13.5.2   Other measurements 					23

13.6     Periodic Calibration					23

13.7     Test Access to Metering Equipment			23

13.8    Records						23

13.9     Location of Meters					23

Performa’s:

Accuracy test result of energy meter		-	Annexure – I		24

Meter removal/replacement/installation		-	Annexure – II		25

C.T Ratio confirmation				-	Annexure – III		26

P.T Ratio confirmation				-	Annexure – IV	27

Discrepancy Report					-	Annexure – V		28

Request to break seals				-	Annexure – VI	29-30

List of Metering points 				-	Annexure-A		A-6

DELHI TRANSCO LTD.

METERING PROCEDURE

Dated  …………………

In compliance to the provisions contained in Delhi Grid code (DGC) Clause No.33 notified by Delhi Electricity Regulatory Commission (DERC) on official Gazette of Delhi on 22.04.2008.   Delhi Transco Ltd. (DTL) being notified as State Transmission Utility in Delhi State makes following procedures for installation and operation of meters namely:

1	Short Titles, extent and commencement

1.1	These procedures may be called “Metering Procedures”.

1.2	These procedures shall be extended to the whole of National Capital Territory of Delhi.

1.3	These procedures shall come into force from the date of its approval by DERC.

2	Definitions

2.1	In these procedures, unless the context otherwise requires;

(a)	‘Act’ means the Electricity Act, 2003;

(b)	‘Accredited Test Laboratory’ means a test laboratory accredited by National Accreditation Board for Testing and Calibration Laboratories (NABL);

(c) 	‘Active Energy’ means the electricity supplied or consumed during a time interval, being the integral of Active Power with respect to time, measured in the units of ‘Watt – hours’ or standard multiples thereof. One ‘kilowatt – hour’ (kWh) is one unit;

(d) 	‘Active Power’ means the electrical power, being the product of root mean square (rms) voltage, root mean square (rms) current and cosine of the phase angle between the voltage and current vectors and measured in units of ‘Watt’ (W) or in standard multiples thereof;

(e) 	‘Availability Based Tariff (ABT)’ means a tariff structure based on availability of generating units and having components, viz, Capacity Charges (CC), Energy Charges (EC) or Variable Charges (VC) and charges for Unscheduled Interchange (UI);

(f) 	‘Buyer’ means any generating company or licensee or consumer whose system receives electricity from the system of generating company or licensee;

(g) 	‘Check Meter’ means a meter, which shall be connected to the same core of the Current Transformer (CT) and Voltage Transformer (VT) to which main meter is connected and shall be used for accounting and billing of electricity in case of failure of main meter;

(h)	`Effective Date’ means the date on which the procedures are approved by the Delhi Electricity Regulatory Commission (DERC).

(i) 	‘Interface Meter’ means a meter used for accounting and billing of electricity, connected at the point of interconnection between electrical systems of generating company directly connected to the Intra State Transmission System who have to be covered under ABT and have been permitted open access by Delhi Electricity Regulatory Commission;

(j)	‘Instrument Transformer’ means the ‘Current Transformer (CT)’, ‘Voltage Transformer’ (VT) and ‘Capacitor Voltage Transformer’ (CVT);

(k) 	‘Main Meter’ means a meter, which would primarily be used for accounting and billing of electricity;

(l) 	‘Meter’ means a device suitable for measuring, indicating and recording consumption of electricity or any other quantity related with electrical system and shall include, wherever applicable, other equipment such as Current Transformer (CT), Voltage Transformer (VT) or Capacitor Voltage Transformer (CVT) necessary for such purpose;

(m)	`Operational Meter’ means a meter for monitoring output and response of power stations, generating units, grid sub-stations of Delhi Transco Ltd. (DTL) and Distribution Licensees for the control of the State Transmission System (STS).

(n) 	‘Power Factor’ means the cosine of the electrical angle between the voltage and current vectors in an AC electrical circuit;

(o) 	‘Reactive Energy’ means, the integral of Reactive Power with respect to time and measured in the units of ‘Volt-Ampere hours reactive (VARh) or in standard multiples thereof;

(p) 	‘Reactive Power’ means the product of root mean square (rms) voltage, root mean square (rms) current and the sine of the electrical phase angle between the voltage complex or and current complex or, measured in ‘Volt – ampere reactive’ (VAr) and in standard multiples thereof;

(q) 	‘Standards’ means ‘Standards on Installation and Operation of Meters’ given in the Schedule of these Regulations unless otherwise any other standard specifically referred;

(r) 	‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter;

(s) 	‘Supplier’ means any generating company or licensee from whose system electricity flows into the system of another generating company or licensee or consumer;

2.2 	The words and expressions used and not defined in these procedures but defined in the Act shall have the meaning assigned to them in the Act.

3	Introduction

This Metering Procedure sets out or refers to the requirements of Interface ABT (including those consumers availing open access or directly connected to the State Transmission System (STS) who have to be covered under the ABT) required to be aligned with the provisions specified under the Indian Electricity Grid Code (IEGC) and DGC of Metering at Generating Stations in Delhi and Substations of DTL as well as sub-station of various distribution licensees.  It will also include metering at Energy exchange points of different licensees and open access consumers in the 220/400KV sub-station of DTL, distribution licensees grid as well as dedicated Generating Stations through out DELHI state.

3.1	The Interface ABT Metering

In the present setup the ABT metering for measurement of active energy (Wh) transmit in each 15 Minute block, reactive energy (VARh) with voltage 103% and above & 97% and below.

a)	DTL system connected to northern Grid including central sector generator at 400/220KV level for Interstate ABT billing.

b)	The dedicated generation of Delhi belonging to Indraprastha Power Generation Company Ltd. (IPGCL), Badarpur Thermal Power Station (BTPS) and Pragati Power Corporation Ltd. (PPCL) are metered at the exchange points mentioned in the Bulk Power Supply Agreement (BSA) executed with DTL at the time of unbundling of erstwhile Delhi Vidyut Board (DVB).

c)	The metering to licensees including consumers availing open access generally done on 66/33 and 11KV with exception. The metering point will be revised from time to time after mutual consultation between stakeholders with the due concern of the commission.

3.1.1	Operational metering

The operational metering shall be provided on each element in the generating/DTL and distribution licensees grid sub-station through displaying equipment to display active, reactive power including Amp, volts, power factor etc.  Each stakeholder shall optimize the metering system so that they are self-dependent to generate their own data base, load flow to enable effective control.

3.2	Objective

DERC being the Power Regulator in Delhi brings together a single set of technical rules, related with metering of energy encompassing all the utilities connected to or using the Intra state ABT billing for commercial and operational purposes.

4  	Specifications and accuracy limits of meters and associated equipment.

4.1 	Functional Requirements for ABT interface meters

(a)	The Interface meters suitable for ABT shall be static type, composite meters, as self contained devices for measurement of active and reactive energy, and certain other parameters as described in the following paragraphs.  The meters shall be suitable for being connected directly to voltage transformers (VTs) having a rated secondary line-to-line voltage of 110V, and to current transformers (CTs) having a rated secondary current of IA (Model-A:3 element 4 wire ) or 5A (Model-B:3 Element, 4 wire).  The reference frequency shall be 50Hz.

(b)	The meters shall have a non-volatile memory in which the following shall be automatically stored:

i)	Average frequency for each successive 15 minutes block, as a two digit code (00 to 99 for frequency from 49.0 to 51.0 Hz).

ii)	Net Wh transmittal during each successive 15 minutes block; upto second decimal with plus / minus sign.

iii)	Cumulative Wh transmittal at each midnight, in six digits including one decimal.

iv)	Cumulative VARh transmittal for voltage high condition, at each midnight, in six digits including one decimal.

v)	Cumulative VARh transmittal for voltage low condition, at each midnight, in six digits including one decimal.

vi)	Data and time blocks of failure of VT supply on any phase, as a star (*) mark.

(c)	The meters shall store all the above listed data in their memories for a period of atleast ten days.  The data older than ten days shall get erased automatically.  Each meter shall have an optical port on its front for tapping all data stored in its memory using a hand held data collection device.  The meter shall be suitable for transmitting the data to remote location using appropriate communication medium.

(d)	The active energy (Wh) measurement shall be carried out on 3-phase, 4 wire Principle, with an accuracy as per class 0.2 S of IEC-687/IEC-62053-22.  In model-A & C, the energy shall be computed directly in CT and VT secondary quantities, and indicated in watt-hours.  In Model-B and Model-D, the energy display and recording shall be one fifth of the Wh computed in CT & VT secondary quantities.

(e)	The Var and reactive energy measurement shall also be on 3-phase, 4 wire principle, with an accuracy as per class 0.2 of IEC - 62053-23 or better.  In Model-A or Model C, the Var and VARh computation shall be directly in CT & VT secondary quantities.  In Model-B or Model-D, the above quantities shall be displayed and recorded as one-fifth of those computed in CT and VT secondary quantities.  There shall be two reactive energy registers, one for the period when average RMS voltage is above 103% and the other for the period the voltage is below 97%.

(f)	The 15 minute Wh shall have a +ve sign when there is a net Wh export from substation busbars, and a -ve sign when there is a net Wh import.  The integrating (cumulative) registers for Wh and VARh shall move forward when there is Wh / VARh export from substation bus bars, and backward when there is an import.

(g)	The meters shall also display (on demand), by turn, the following parameters:

(i)	Unique identification number of the meter.

(ii)	Date

(iii)	Time

(iv)	Cumulative Wh register reading with +/- sign

(v)	Average frequency of the previous 15 minute block.

(vi)	Net Wh transmittal in the previous 15 minute block, with+/-sign

(vii)	Average percentage voltage

(viii)	Reactive power with +/- sign

(ix)	Voltage-high VARh register reading

- Voltage-low VARh register reading.

(h)	The three line-to-neutral voltages shall be continuously monitored, and in case any of these falls below 70%, the condition shall be suitably indicated and recorded.  The meters shall operate with the power drawn from the VT secondary circuits, without the need for any auxiliary power supply.  Each meter shall have a built-in calendar and clock, having an accuracy of 30 seconds per month or better.

(i)	The meters shall be totally sealed and tamper-proof, with no possibility of any adjustment at site, except for a restricted clock correction.  The harmonics shall be filtered out while measuring Wh, Var and VARh, and only fundamental frequency quantities shall be measured/computed.

(j)	The main meter and the check meter shall be connected to same core of CTs and VTs.

4.1.1 Instrument Transformers

(a) 	All current transformers and voltage transformers used in conjunction with the ABT metering shall conform to relevant Indian Standard Specifications or relevant IEC.

(b)	The accuracy class of Current transformers (CTs) and Voltage transformers (VTs) shall not be inferior to that of associated meters.  The existing CTs and VTs not complying with these regulations shall be replaced by new CTs and VTs, if found defective, non functional or as per the directions of the appropriate Commission.  In case the CTs and VTs of the same accuracy class as that of meters cannot be accommodated in the metering cubicle or panel due to space constraints, the CTs and VTs of the next lower accuracy Class can be installed.

Note:- IEGC states that C.T’s/V.T’s shall have accuracy class of 0.5 or better.

(c)	The Voltage Transformers shall be electromagnetic VT or Capacitive Voltage Transformer (CVT).

4.1.2 Overall Accuracy of Equipment

Existing Metering shall be calibrated, so as to achieve Overall Accuracy of Interface Metering within the limits of Class 1.0. Even if all CT/PT individually found okay but overall accuracy is beyond class 1.0, the metering system will be treated as defective.  All CT and PT in a metering system should have identical class of accuracy.

4.2 Functional Requirements for Audit and Accounting meters:

(1)The energy accounting and audit meters shall be suitable for measurement, recording and display of cumulative active energy with date and time.

(2)The energy accounting and audit meters may also have the facility to measure, record and display one or more of the following parameters depending upon the energy accounting and audit requirement. All parameters excluding instantaneous electrical parameters shall also be stored in memory.

  - Apparent power

  - Phase wise kilowatt at peak KVA

  - Phase wise KVA(reactive) at peak KVA

  - Phase wise voltage at peak KVA

  - Power down time

  - Average power factor

  - Line currents

  - Phase voltages

  - Date and time

  - Tamper events

  - Cumulative apparent energy (KVAh)

  - Any other parameter required for tariff application or analysis.

(3)The energy accounting and audit meter shall have data storage capacity for at least 35 days in a non-volatile memory.

(4)Energy accounting and audit meters shall have facility to download the parameters through meter reading instruments as well as remote transmission of data over communication network.

4.3 Standards

All interface ABT meters and energy accounting and audit meters shall -

(a) Comply with the relevant standards of Bureau of Indian Standards (BIS), If BIS Standards are not available for particular equipment or material, the relevant British Standards (B), International Electro-technical commission (IEC) Standards, or any other equivalent Standard shall be followed:

Provided that whenever an international Standard or IEC Standard is followed, necessary corrections or modifications shall be made for nominal system frequency, nominal system voltage, ambient temperature, humidity and other conditions prevailing in India before actual adoption of the said Standard.

(b) Confirm to the requirements of CEA (Installation of Meters & Operation of meters  Regulations 2006 dated 17.03.06 & Amendment Regulations 2010 dt. 04.06.10) standards prescribed there under and as amended from time to time.

5.0	Location of Meters

The meters shall be mounted on the respective control panel of transformer/feeder in the Control Room.

- Interface Meters :- (a) The location of interface meters shall be as specified in Table-1

Provided that the location of main, check and standby meters installed at the existing generating stations shall not be changed unless permitted by the Authority.

Provided further that the generating companies or licensees may install meters at additional locations in their systems depending upon the requirement.

Table-1

| Sl.No. | Stages | Main Meter | Check Meter | Standby Meter |
| --- | --- | --- | --- | --- |
| (1) | (2) | (3) | (4) | (5) |
| 1. | Generating Station | On all outgoing feeders | On all outgoing feeders | (i)High Voltage (HV) side of Generator Transformers (ii)High Voltage (HV) side of all Station Auxiliary Transformers |
| 2. | Transmission and Distribution System | Metering between Delhi Transco Limited and different licensees. (i) The metering of energy to licenses from DTL 220kV Sub-Station shall be carried out on the LV voltage (66 or 33 kV) as the case may be, there could be Sub-Station where:- a) Entire energy is delivered to one licensee in such case the dedicated metering equipment shall be installed on each EHV Transformer (220/66/33 kV) on the LV side through dedicated CTs and relevant Bus VTs. b) In second case where stakeholders are more than one, the energy shall be measured on each feeder pertaining to a particular licensee through dedicated CTs and relevant Bus VTs. c) The energy utilized by DTL for auxiliary equipment at 220 kV Sub-Station shall be metered on 11 kV side of the Transformer. d) The Capacitor Bank installed on 66, 33 and 11 kV Buses of DTL Sub-Station shall be provided with a reactive energy meter. e) Some of the DTL grids due to their geographical location serve a licensee dedicatedly but the 66/33 kV feeders interconnect to DTL Sub-Station which are not serving the same licensees. In such cases a suitable Sub-Station belonging to a DISCOM / Licensees should be made as inter company exchange point and the metering equipment shall record import and export energy. The metering equipment provided by Delhi Transco Limited on 66/33 kV interconnection points between different Discoms / Licensees are provided with ABT metering by DTL. Where as on 11kV exchange points between Discoms/Licensees the ABT meters responsibility lies on DTL. f) The 220KV Grid Sub-Station is the territory of NCR which do not belong to DTL but to a third party, the metering equipment shall be provided by DTL on L.V side of EHV Transformer (220/66/33kV), the metering shall be either on incomer of the Transformer if dedicated to one stakeholder. In case the stakeholder are more than one in that case all feeders belonging to a licensees shall be metered through dedicated CTs and Bus PTs. g) Where a grid Sub-Station belonging to a particular licensee receive Power from different DTL Sub-Station and transfer power to other Discoms, the metering arrangement shall be provided by DTL and the bus arrangement shall be maintained as decided by DTL. All electrical operation in the Sub-Station shall be on the directive of DTL. |
| 3. | Inter-Connecting Transformer | High Voltage side of Inter-connecting Transformer | - | Low voltage side of inter connecting Transformer |

(b) The scheme for location of interface meters shall be submitted to the Central Transmission Utility or the State Transmission Utility or the licensee by owner of the meter in advance, before the installation of the scheme .

- Energy accounting and audit meter.- The Energy accounting and audit meters shall be installed at following locations to facilitate the accounting of the energy generated, transmitted, distributed and consumed in various segments of the power system and the energy loss, namely:-

  - Generating Stations.-(a) at a point after the generator stator terminals and before the tap-off to the unit auxiliary transformer(s),

    - on  each  incoming  feeder  of  3.3  kV  and  above.

    - low voltage side of each incoming transformer feeder of low voltage (415 V) buses, and

    - on  all  high  tension  motor  feeders.

Provided that in case, numerical relays having built-in feature of energy measurement of requisite accuracy are provided in high voltage or low voltage switchgear, separate energy meter is not necessary.

- Transmission system.- all incoming and outgoing feeders (if the interface meters do not exist)

(iii)  Distribution  system.-   (a)  all  incoming  feeders(11  kV  and  above)

(b) all  outgoing  feeders  (11  kV  and  above)

(c) Sub-station transformer including distribution transformer- Licensee may provide the meter on primary or secondary side or both sides depending upon the requirement for energy accounting and audit.

5.1  	Installation

DTL shall install a Main meter and a Check meter at all of its 400kV and 220kV Sub-Stations on which any point of supply situated

5.2	Following Responsibility

Following installation, the Main meters and the Check meter shall be the property of DTL and DTL shall be responsible for the cost of their maintenance, replacement and calibration. All the meters mentioned in this clause 3.1 shall be under the joint custody of the parties.

Notwithstanding the above metering system, parties expressly agree and accept that DTL shall own the 66kV bus bars (or the 33kV bus bars in case the point of supply is at 33kV) at the 400 kV or 220 kV substations on which any point of supply is situated and shall be responsible for their operation and maintenance.

5.3	Metering between Delhi Transco Limited and different licensees.

(i)	The metering of energy to licenses from DTL 220kV Sub-Station shall be carried out on the LV voltage (66 or 33 kV) as the case may be, there could be Sub-Station where:-

a)	Entire energy is delivered to one licensee in such case the dedicated metering equipment shall be installed on each EHV Transformer (220/66/33 kV) on the LV side through dedicated CTs and relevant Bus VTs.

b)	In second case where stakeholders are more than one, the energy shall be measured on each feeder pertaining to a particular licensee through dedicated CTs and relevant Bus VTs.

c)	The energy utilized by DTL for auxiliary equipment at 220 kV Sub-Station shall be metered on 11 kV side of the Transformer.

d)	The Capacitor Bank installed on 66, 33 and 11 kV Buses of DTL Sub-Station shall be provided with a reactive energy meter.

e)	Some of the DTL grids due to their geographical location serve a licensee dedicatedly but the 66/33 kV feeders interconnect to DTL Sub-Station which are not serving the same licensees.  In such cases a suitable Sub-Station belonging to a DISCOM / Licensees should be made as inter company exchange point and the metering equipment shall record import and export energy.  The metering equipment provided by Delhi Transco Limited on 66/33 kV interconnection points between different Discoms / Licensees are provided with ABT metering by DTL.  Where as on 11kV exchange points between Discoms/Licensees the ABT meters responsibility lies on DTL.

f)	The 220KV Grid Sub-Station is the territory of NCR which do not belong to DTL but to a third party, the metering equipment shall be provided by DTL on L.V side of EHV Transformer (220/66/33kV), the metering shall be either on incomer of the Transformer if dedicated to one stakeholder. In case the stakeholder are more than one in that case all feeders belonging to a licensees shall be metered through dedicated CTs and Bus PTs.

g)	Where a grid Sub-Station belonging to a particular licensee receive Power from different DTL Sub-Station and transfer power to other Discoms, the metering arrangement shall be provided by DTL and the bus arrangement shall be maintained as decided by DTL.  All electrical operation in the Sub-Station shall be on the directive of DTL.

5.4	Notice of Installation of New Meters

Timely Installation

Where notice is served on DTL, an interested party of an existing Relevant Connection site, which is the point of supply of a Distribution licensees, the proposed interested party shall confirm that metering required for the purposes of this Metering procedure will be installed and kept operational at the Relevant connection site.  Where the necessary metering will not be installed and operational by a required date, the interested party and DTL shall follow the provisions set out in such Metering shall be tested in accordance with the provisions of Metering procedure.

6.0	procedure to ensure conformance to the accuracy limits, TESTING AND REPLACEMENT OF METERS.

6.1	Procedure and Periodicity

a)	At the time of commissioning, each interface meter shall be tested by the owner in the presence of concerned licensee / stake holder at site for accuracy using standard reference meter of better accuracy class than the meter under test.

b)	All interface meters shall be tested at least once in five years. These meters shall also be tested whenever the energy and other quantities recorded by the meter are abnormal or inconsistent with electrically adjacent meters. Whenever there is unreasonable difference between the quantity recorded by interface meter and the corresponding value monitored at the billing center via communication network, the communication system and terminal equipment shall be tested and rectified. The meter testing shall be supervised by representatives authorized by the metering committee and preferably shall be tested using NABL accredited mobile laboratory or at any accredit laboratory and recalibrated if required at manufacturers work.

(c)	Testing and calibration of interface meters may be carried out in the presence of the representatives of the supplier and buyer.  The owner of the meter shall send advance notice to the other party regarding the date of testing.

6.2	Procedures associated with maintenance of the meters proper functioning state

The operation, testing and maintenance of all types of meters shall be carried out by the DTL or the licensee, as the case may be.

6.3		Inspection and Testing of Meters

6.3.1	Testing of Main and Check Meter

The Main and the Check Meters shall be calibrated or tested in the presence of the representatives of concerned licensees and DTL.  Each party shall ensure that the meters, monitors, terminals of CT and PT, are appropriate and the associated circuits with it owns, are sealed between inspections and tests.

    - Accuracy/Check and Test Performa

The accuracy of the meters shall be verified jointly in accordance to IS standards and filled up in prescribed Performa (Annexure-I). Similarly instrument transformers ratio’s be confirmed (Annexure-III&IV) followed by meter installation Performa including verification of its functioning (Annexure-II).

The Company and DTL shall inspect the metering system at least once every 5 years. Any party can require the testing of any Meter even before the period of 5 years stipulated above. In such a case, if after the test, the meter is found to be within the accuracy levels required by this schedules, the cost of meter testing shall be borne by the party who had requested for the test. In all other cases, the cost of the meter test and recalibration shall be borne by the owner of such meter.

In addition to the tests conducted under relevant clause in the event that the reading on the check meter differs from that on the Main meters by more than + 0.5% in any month, the Main meters and the Check meters shall be jointly tested in turn.

6.3.3	Defective Meter replacement

In the event that any meter comprising the meter system is found to be defective, it shall be obligatory for DTL to recalibrate or replace the meter within seven (7) days to ensure that it is functioning correctly.

6.4	Safety of meters

(1) 	The supplier or buyer in whose premises the interface meters are installed shall be responsible for their safety.

(2)	The consumer shall, as far as circumstances permit, take precautions for the safety of the consumer meter installed in his premises belonging to the licensee.

(3)	Licensee shall be responsible for the safety of the consumer meter located outside the premises of the consumer and the consumer shall be responsible for the safety of the real time display unit installed by the licensee in consumer premises.

(4)	The generating company or the licensee who owns the energy accounting and audit metes shall be responsible for its safety.

6.5  	Sealing of meters

6.5.1 	Sealing Arrangement

(a)	All meters shall be sealed by the manufacturer at its works. In addition to the seal provided by the manufacturer at its works, the sealing of all meters shall be done as follows at various sealing points as per the standards given in the schedule.

(i) 	Sealing of interface meters, shall also be done by both the supplier and the buyer.

b)	Seal shall be unique for each DISCOM, DTL, generating company etc. and name or logo of the Owner shall be clearly visible on the seals.

c)	Only the patented seals (seal from the manufacturer who has official right to manufacture the seal) shall be used.

d)	Polycarbonate or acrylic seals or plastic seals or holographic seals or any other superior seal shall be used.

e)	Lead seals shall not be used in the new meters. Old lead seals shall be replaced by new seals in a phased manner and the time frame of the same shall be submitted by the DTL to the appropriate commission for approval.

f) 	The type of seal going to be used by each company shall be informed to Metering Committee.

6.5.2  	Removal of seals from Meters

Whenever seals of the interface metes have to be removed for any reason, advance notice as per Performa at Annexure-VI shall be given to other party for witnessing the removal of seals and resealing of the interface meter. The breaking and re-sealing of the meters shall be recorded by the party, who carried out the work, in the meter register, mentioning the date of removal and resealing, serial numbers of the broken and new seals and the reason for removal of seals.

6.5.3 	Inspection of meters.

The main meters and the check meters and any other meter relevant to the calculations of the payments due shall be sealed with a seal owned by each of the parties and shall not be opened. Meter shall be calibrated or tested in the presence of the representatives of the companies and DTL. Each party shall ensure that the meters, monitors, terminals of CT and PT, are appropriate and the associated circuits which it owns, are sealed between inspections and tests.

7.	Provisions related to right of access to the meter

7.1	Right of Access

The owner of the premises where, the meter is installed shall provide access to the authorized representative(s) of the licensees and the representatives authorized by the Metering Committee for installation, testing commissioning, reading and recording and maintenance of meters.

7.2	Access with Equipment

The right of access provided includes the right to bring in such vehicles, plant, machinery, test kits and maintenance or other materials as shall be necessary for the purposes of this Metering procedure.

7.3	Authorization for Access

Each Party shall ensure that any particular authorization or clearance for any person which is required to be given to ensure access is available on the arrival of such person at the relevant site.

7.4	Limiting Disruptions and Disturbances

Subject to the right of DTL to inspect without notice each Party shall ensure that all reasonable arrangements and provisions are made and/or revised from time to time, as and when necessary or desirable, to facilitate any right of access with the minimum of disruption, disturbance and inconvenience.  Such arrangements and provisions made to a reasonable extent limit or restrict the right of access and/or provide for any party to make directions or regulations from time to time in relation to a specified matter.

7.5	Safety Procedures

Each person/employee granted access shall observe and comply with any such safety arrangements and all provisions (or directions or regulations issued pursuant thereto) that are made from time to time.

7.6	Responsibilities of Access

Each party granted access shall ensure that all reasonable steps are taken in the exercise of any right of access to:

(a)	Avoid damage in relation to the property over which they have access, and

(b)	Cause as little disturbance and inconvenience as possible to any party or other occupier of such property, and shall make good and damage caused to any such property in the course of exercising such rights, as soon as may be practicable.  Subject to this, all such rights of access shall be exercisable free of any charge or payment of any kind.

8.	RIGHTS, RESPONSIBILITES AND PROCEDURES RELATED TO RECORDING, COLLECTION, tRANSFER, PROCESSING AND STORAGE OF DATA COLLECTED FROM METERS:

8.1	Rights

Each party shall grant to any other party, its employees, agents and contractors and persons duly authorized by them full right to enter and remain upon any party of such Party’s property to the extent necessary for the purposes of this Metering Procedure.  Each party granting access must further ensure that any consent or other forms of approval granted remain valid at the time of such access including, if appropriate rights of access across third party land.

The right of access includes the right to bring in such vehicles, plant, machinery, test kits, loading kits etc. and maintenance or other materials as shall be necessary for the purposes of this Metering Procedure.

8.2	Responsibilities and procedures related to recording, collection, transfer, processing and storage of data collected from meters

It would be responsibility of SLDC to maintain all energy accounting as per provisions of Act.  The energy meters as installed under the Metering Procedure by DTL being STU at all energy exchange points.  The UI accounting under Intrastate ABT is a weekly process and energy meter readings are to be down loaded by each party and communicated periodically to SLDC which would compute the actual net drawl of each beneficiary for each 15 minute time block as per the provisions of IEGC and prepare UI accounts.  The UI accounts along with the energy meter data would be uploaded in SLDC’s website for information of all stakeholders.

9.  	PROVISIONS RELATED TO OWNERSHIP OF METERING DATA

It is the responsibility of SLDC to keep account of quantity release to each party though out the State and the ownership would be responsibility of SLDC.  The data for the preceding months would be available to each DISCOM’s on request if required for meaningful purpose decided by SLDC.

10.	PROCEDURE TO ADDRESS METERING DISCREPANCIES, DEFECTIVE EQUIPMENT AND METER FAILURE.

10.1.		To Address Metering Discrepancies

When any party acknowledge any inaccuracy or discrepancy in metering the reports of such meter readings will be provided to the Interested Party and any resulting discrepancies will be dealt with as provided in the relevant procedure.  In any other circumstances where metering is not complying with the standards required by this Metering Procedure such difference will be dealt with in accordance with.

As far as possible settlement values shall be derived from the meters readings.

10.2.	Defective meters

If at any time any meter is destroyed or damaged, or otherwise ceases to function, or is found to be outside the prescribed limits of accuracy, the Interested Party shall, subject to compliance with its obligations, promptly, renew or, repair the same or replace any defective component so as to ensure that the relevant Meter is restored to service and operating within the prescribed limits of accuracy within one month from the date of noticing the defect.   Meter includes the secondary circuits of instrument transformers.

10.3      Meter Failure

10.3.1 	Assumed Meter Readings in the event of Faulty metering

If at any time, Metering ceases to function or is found to be outside the prescribed limits of accuracy for whatever reason, or

10.3.2	Non-Functioning of Metering

In the case of Metering ceasing to function, during the period from the date of such cessation; or

10.3.3	Other Cases of Inaccuracy and Resolution

In any other case, during the period from the time when such inaccuracy first occurred or, if such time is unknown, from the midnight preceding the day during which the disputed reading occurred, until the date of adjustment or replacement, repair or renewal of such Metering then the meter readings shall be deemed to be those calculated pursuant near to realistic value on the basis of load, voltage, power factor and duration of the case may be and in the case of disputes, the following shall be referred.

In the event that any Main Meter fails to register or, upon being tested, is found not to be accurate within + 0.2% but the Check meter is found to be accurate within + 0.2%, the electrical energy shall for the relevant period be measured on the basis of the value registered by the corresponding Check meter.

In the event that the Main Meter and the corresponding Check Meter both fail to register or, upon being tested, be found not to be accurate within + 0.2%, the electrical energy shall for the relevant period be adjusted by immediately restoring and recalibrating the Main Meter and the corresponding Check Meter and the correction applied to the consumption registered by the Main Meter.

For the purpose of the correction to be applied, the Main Meter shall be tested at 120, 100, 50 and 20 per cent load at unity power factor and 0.5 power factor lag.  Of these values, the error at the load and power factor nearest the average monthly load served at the points of Supply during the relevant period shall be taken as the error to be applied for correction.

The print out of data and readings recorded in the memory of static energy meters, down loaded through meter reading instrument or otherwise shall also be recognized for the computation of energy and such other action as may be deemed necessary.

The relevant period referred to in the above clauses shall be the actual period during which inaccurate measurements were made if such period can be determined or, if not readily determinable, the shorter of (i) the period since the immediately preceding test of the relevant Main Meter and (ii) ninety (90) days immediately preceding the test at which the relevant Main Meter was determined to be defective or inaccurate.

10.3.4	Voltage Transformer Fusing

If any time a voltage transformer fuse or voltage selection relay on a circuit supplying a meter has failed with the result that the Metering is outside the prescribed limits of accuracy, the meter readings from the time the failures deemed to have occurred until the voltage transformer circuit is again restored to the meter, shall be deemed to be those calculated pursuant near to the realistic value on the basis of load, voltage, power factor and duration or the case may be, and in the case of disputes, shall be referred.

11  	PROCEDURE FOR RESOLUTION OF DISPUTES ON METERING

11.1	Disputes

11.1.1  General

Any dispute relating to metering which would affect any payment to be made or reduced in respect of a Generating company / distribution licensee shall be dealt with in accordance with the relevant Disputes procedure.

11.1.2 	Referrals to the Metering Committee

Any dispute in relation to the following matters shall be referred to the Metering Committee and if not resolved in the Metering Committee then referred to the Commercial Sub-Committee created under Grid Coordination Committee (GCC) envisaged in Delhi Grid Code.  If the dispute is not resolved in the Commercial Sub-Committee, the matter would be referred to GCC whose decision shall be final and binding and shall be communicated to all parties concerned.

(a)    	Location of metering

(b)	Technical specifications for Metering and associated installations like measuring transformers.

(c)   	Sealing of Tariff Metering.

(d)  	Compliance of Metering or Measuring Transformer with technical specifications of the Metering Code.

(e) 	Any other issue pertaining to interface metering which a party may raise.

(f)  	Procedure for Other Disputes

Any other dispute not covered under this Metering Procedure shall be dealt with in accordance the disputes procedure in the relevant connection Agreement.

(g) 	Testing of metering

Any testing of metering or measuring transformers required to settle a dispute shall be carried out in accordance with 10.3.3.

(h) 	Payment of Costs

The metering Committee shall have the power to order payment of costs and expenses in respect of any dispute referred to it in such manner, as it considers appropriate. The Metering Committee shall have the power to demand any information it may properly and reasonably require to settle a dispute from any Party and such Party shall provide the relevant information on request.

11.2     Metering Committee

11.2.1 	Composition of the Metering Committee

The Metering Committee shall be appointed for the purposes of this Metering Procedures.  The composition of the Metering Committee shall be decided by the Commercial Sub Committee created under Grid Coordination Committee (GCC) envisaged in Delhi Grid Code.

11.2.2 	Communicating Revisions to the Metering Code

If, during any commercial sub committee meeting or GCC, it is decided to revise any part of the Metering Procedure, the decision shall be communicated in writing to the concerned committees.  If the GCC approves the revised Metering Procedure, the same shall be forwarded to DERC for approval.  The revised Metering Procedure shall be made affective from the date of the approval of revised Metering Procedure by DERC.

11.3   	Information

11.3.1 	Provision of Information to DELHI TRANSCO LTD.

All Parties shall give to DELHI TRANSCO LTD. all such information in their possession regarding metering which DTL shall reasonably require for the proper functioning including information regarding the dates and time periods for installation of new metering and the dates and periods when metering will be out of service.

11.3.2	Dispute Resolution

At the request of any Party which is a party to the dispute, any relevant data associated with the Metering in question shall be submitted by DELHI TRANSCO to the Metering Committee for the purpose of resolving such dispute.

11.4  	Ownership of Metering Data

The interested party of any Metering shall own the data acquired there from. Any Party shall at all times have the right to access to the data and to use the same as may be permitted pursuant to this Metering Procedure free of charge.  If the data is confidential, the party may only release such data to others to the extent required pursuant to this Metering Code or as permitted by the Connection Agreement.

11.5  	Settlement of Disputes

The interested party and DTL shall agree demand settlement values for each demand settlement period, for each day from the expiry of the notice until the relevant Metering is installed and operational.

If agreement cannot be reached within 14 days, the matters may be referred to arbitration in accordance with the relevant Connection Agreement and payments will be made on the basis of values as reasonably determined by DTL pending a decision of the arbitrator.  Payments shall be adjusted as appropriate at the time of such decision to take into account the Settlement values so determined since the date of such notice;

DTL shall take all such values into account and the interested party shall be bound to accept such values, for the purpose of electricity consumption until the relevant metering is installed and operational:

12       	Others

12.1     Amendments to Performa’s

Performa’s set out in the Appendices to this Procedure may be amended from time to time by DTL upon reasonable notice to all Interested Parties.  DTL shall also take into account the reasonable comments of Interested Parties.  DTL shall put up the proforma to Commercial Sub-Committee for approval and in case Commercial sub-committee could not finalize the proforma, the matter would be referred to GCC for decision.

12.2   	Provision of Information to DELHI TRANSCO LIMITED

All Parties shall give to DTL all such information in their possession regarding metering which DTL shall reasonably require for the proper functioning including information regarding the dates and time periods for installation of new metering and the dates and periods when metering will be out of service.

12.3   	Dispute Resolution

At the request of any Party which is a party to the dispute referred for any relevant data associated with the Metering in question shall be submitted by DTL to the Commercial sub committee for the purpose of resolving such dispute and  in case Commercial sub-committee could not resolve the dispute, the matter would be referred to GCC for decision.  The decision of GCC shall be binding upon all parties.

12.4   	List of Intra State ABT Meters

The list of meters using for energy accounting purposes at present is enclosed collectively as Annexure-A.

13	OPERATIONAL METERING

13.1	Scope

It specifies the facilities that shall be provided and the certain practices that shall be employed, for monitoring output and response of Power Stations, Generating Units, Grid Sub-Stations of DTL and distribution licensees for the control of the STS.

13.2	Standards

All references to industry standards which are currently at the effective date.  Where Operational metering is in use at the effective date which was installed when earlier version of these standards (or their predecessors) were in force there is no requirement to update such Operational Metering unless expressly required.

Operational Metering installed after the Effective Date is required to comply with the version of any such standard in force on the date of installation.

Robustness and reliability are the most important attributes required for Operational Metering.

13.3	Operating Characteristics

SLDC shall have the right to advise the Generating Co., Distribution licensees and open access consumer to install Operational Metering so as to provide operational information in relation to each Generating unit and each power station, grid Sub-Station, power transformer, lines etc.

Information as required by SLDC, under the section 33(1) of Indian Electricity Act 2003, shall be presented continuously through Supervisory Control and Data Acquisition System (SCADA).

  - Metering components

13.4.1	Energy meter:

The meter shall be of class 0.5 or better.  The meter shall measure all parameters in general required for grid audit, control and monitoring purpose. The meter shall be capable enough to provide information desired by SLDC from time to time.

13.4.2	Current Transformers

Current Transformers installed after the Effective Date shall comply with latest versions of ISS 2705/1992, IEC 185, and IEC 44-4 accuracy class not inferior to the meter installed and have a rated output of not less than 15 VA.

The Current Transformer secondary winding used for purposes of Interface and Operational Metering so long as such do not degrade the required accuracy outside limits (as required for interface metering).

13.4.3	Voltage Transformers

Voltage Transformers installed after the Effective Date shall comply with ISS 3156 - 1992 IEC - 186 (1987) accuracy not inferior to the meter installed and have a rated output of not less than 100VA per phase.

The voltage transformer secondary winding used for purposes of Interface and Operational Metering providing such do not degrade the required accuracy outside the limits (as required for interface metering).

### 13.4.4	Power Supplies

Operational Metering at Power Station shall be connected to assured power supplies.  Where assured power supply is not available, voltage selection schemes shall be installed to support Operational Metering.

13.5	Overall Accuracy of Equipment

Metering shall be calibrated, so as to achieve Overall Accuracy of Operational Metering within the limits for meters of class 2.0.

## 13.5.1	Accuracy of Time keeping

The time keeping accuracy of Operational Metering shall be maintained in accordance with standard time.

## 13.5.2	Other Measurements

Overall accuracy requirements for all other electrical and non-electrical parameters shall be as determined by DTL with the agreement of the Commission after consultation with all Interested Parties.

13.6	Periodic Calibration

Operational Metering shall be tested not less than once in every five (5) years or otherwise as advised by the Commercial Sub Committee having regard to an acquired knowledge of the performance of the particular design of Operational Metering.

Operational metering shall be recalibrated following any adjustment or test.

13.7	Test Access to Metering Equipment

Test terminal blocks in accordance with ISS shall be provided to facilitate Operational Metering testing and/or current and voltage transformer checks.  Non-electrical parameters shall be tested as agreed between DTL and the relevant Interested Party.

13.8	Records

The results of all calibration tests and recalibrations on Operational Metering and all periodic checks or recalibrations shall be kept for Inspection at least for one year.

13.9	Location of Meters

The meters shall be mounted on the respective control panel of transformer/feeder in the Control Room.

GENERAL MANAGER (O&M)

DELHI TRANSCO LTD.

New Delhi

Dated :

Annexure-I

DELHI TRANSCO LTD.

(Office of Manager(ICM), Park Street, New Delhi.)

# ACCURACY TEST RESULTS OF ENERGY METER (MAIN/CHECK)

## Date of Testing                            _________________

Time of Start	                    _________________

Time of Completion                  _________________

- Name of the Grid	__________________________________	 	                                           Duration			           _________________

- Name of Feeder	__________________________________       	B:-  STANDARD METER DETAIL

- Voltage level	__________________________________		                 		Make :- 		_____________

# A :- DETAIL OF METER UNDER TEST                                                      		S.No. ______________

(a)	S.No.		          ______________	(h) Class of Accuracy   0.2 		Accuracy Class =_____

(b)	Make 		               ELSTER          (i)  Wh/Impulse         _______

(c)	Type		          ALPHA(M+)	(j)   M.F.(O/A)           _______	Meter  Display Parameters

|  | At Start | On Completion |
| --- | --- | --- |
| Time |  |  |
| V1 (Volt) |  |  |
| V2 (Volt) |  |  |
| V3 (Volt) |  |  |
| I1 (Amp.) |  |  |
| 12 (Amp.) |  |  |
| I3 (Amp.) |  |  |
| PF |  |  |

(d)	C.T.(D)       ____________    	(k)  Yard  (i)  CTR  :      ___________

(e)	P.T.(D)                     ___________                   (ii)  PTR :   __________

(f)	M.F.(D)	         ____________

(g)	Unit		                  KWH

NOTE:-	The meter tested under shutdown/ without S/D by shorting C.T’s sec.

D:-  TEST RESULTS : -		ACTIVE ENERGY

| S.No. | Injected Current | UPF 0.5 Lag |
| --- | --- | --- |
|  |  | Error | Standard Meter”E” | Actual Error | Acceptable limit of error as per IS 14697:1999 Clause 11.1 | Error | Standard Meter”E” | Actual Error | Acceptable limit of error as per IS 14697:1999 Clause 11.1 |
| 1. | 100% |  | 0.015 |  | 0.2 |  | 0.015 |  | 0.3 |
| 2. | 80% |  | 0.014 |  | 0.2 |  | 0.014 |  | 0.3 |
| 3. | 50% |  | 0.013 |  | 0.2 |  | 0.013 |  | 0.3 |
| 4. | 20% |  | 0.014 |  | 0.2 |  | 0.013 |  | 0.3 |

Reading:

| R. Code At Start | On Completion |
| --- | --- |
| 004 (KWH) |  |
| 005 (KvArh) |  |
| 006 (KvAh) |  |
| 009 (KWH) |  |
| 010(KvArh) |  |
| 011(KvAh) |  |

Exp

Imp Remarks______________________________________________________________________________

Detail of seal__________________________________________________________________________________________

Witnessed by:				               			Tested by:

Signature     __________________                       				Signature     ____________________

Name           __________________                                                		Name           ____________________

Designation ________Of  NDPL/ BRPL/BYPL/MES/NDMC	     		Designation ___________ Of DTL (Transco)

ANNEXURE.II

DELHI TRANSCO LTD

(Office of Manager(ICM), Park Street, New Delhi.)

METER  REMOVAL/REPLACEMENT/INSTALLATION  SHEET

01.   Name of Grid   	________________________          	02.  	Name of the Feeder   	______________________________

##### 03.  Location of the Meter  	___________________________         		04.  	Voltage Level             	__________________________________

(OLD)                   (NEW)                                 	                                     	(OLD)                         (NEW)

05.  S. No. of Meter     	_____________    _____________   	06.  	Type/Pulse Rate      	__________ ALPHA(M+)/0.12Wh/Imp.

07.    Meter Make        _____________           ELSTER       	08.  	Class of accuracy    	______________    ________________

09.    Status	        	 MAIN _____                    CHECK     	Dial Factor/Unit        	______________    ______1000 / KWH___

11.    (a)  CTR                : ____________    ______________  	              Yard  (a) CTR          :  ______________

(b)  PTR                : ____________    _____________                              (b) PTR          :  ______________

12.   Reading M.F.        :  ____________   ______________

13.   METER READING DATA                                             		Energy Assessment Data

(When main meter was out of Service with loaded feeder)

| OLD | NEW |
| --- | --- |
| UNIT | READINGS | UNIT Id No. | READINGS |
| MWh |  | 004 | KWh Delivered |  |
| MVARh(Lag) |  | 005 | KVARh “ |  |
| MVARh(Lead) |  | 006 | KVAh “ |  |
| MVAh |  | 009 | KWh Recd. |  |
|  |  | 010 | KVARh “ |  |
|  |  | 011 | KVAh “ |  |
|  | At Start | On Completion |
| Time |  |  |
| I1 (Amp.) |  |  |
| I2 (Amp.) |  |  |
| I3 (Amp.) |  |  |
| V1 (Volts) |  |  |
| V2(Volts) |  |  |
| V3 (Volts) |  |  |
| P.F. |  |  |

14.    Date and time of replacement on  ______/_________/_________/ at _______________________Hrs.

15.     Reason for replacement) :      ________________________________________________________________________________________________________________

16.     Provision  of Seals                  ________________________________________________________________________________________________________________

17.     Remarks                                   ________________________________________________________________________________________________________________

________________________________________________________________________________________________________________

Signature                                 _________________________________                    Signature    ______________________________

Name                                        _________________________________                    Name           ______________________________

Designation 		           _______of NDPL/ BRPL/BYPL/NDMC/MES	Designation _________________________of DTL

ANNEXURE.III

DELHI TRANSCO LIMITED

(Office of Manager (ICM), Park Street, New Delhi.)

CT RATIO CONFIRMATION AT INTER COMPANY

EXCHANGE POINT

Date					___________________________ 		        	Time		_________________

Name of Grid substation		___________________________			Standard injection meter Detail

Name of Feeder				____________________________			Sr. No. 		_____________________________________

CT Ratio as per Name Plate		____________________________			Make		__________ Accuracy Class______________

CT Ratio Printed on Panel		_____________________________			Validity	_____________________________________

| Phase | Sr. No | Make | VA Burden | Accuracy Class |
| --- | --- | --- | --- | --- |
| R |  |  |  |  |
| Y |  |  |  |  |
| B |  |  |  |  |

| INJECTED CURRENT IN AMPERES | OUTPUT RATIO AND PHASE DISPLACEMENT |
| --- | --- |
|  | `R’ PHASE | `Y’ PHASE | `B’ PHASE |
|  | RATIO ERROR | PHASE DISPLACEMENT | RATIO ERROR | PHASE DISPLACEMENT | RATIO ERROR | PHASE DISPLACEMENT |
| 1 (120%) |  |  |  |  |  |  |  |
| 2 (100%) |  |  |  |  |  |  |  |
| 3 (20%) |  |  |  |  |  |  |  |
| 4 (5%) |  |  |  |  |  |  |  |
| Overall Ratio Error | _______% | _______% | _______% |
| Over All Phase Angle Error | _______% | _______% | _______% |
| Burden (as found) | ______VA | ______VA | ______VA |

OVERALL CTR 						____________________________________ERROR %	_________________

CONCLUSION							_______________________________________________________________

REMARKS							_________________________________________________________________

Rep. Of NPDL/BYPL/BRPL/NDMC/MES	                Rep. Of DTL

Sig.	_________________	                                 	    __________________

Name	________________                                     	    __________________

Deign.	_________________	                                  	    __________________

ANNEXURE.IV

DELHI TRANSCO LIMITED

(Office of Manager (ICM), Park Street, New Delhi

PT RATIO CONFIRMATION AT INTER COMPANY

EXCHANGE POINTS

Date					___________________________ 		        	Time		_________________

Name of Grid substation		___________________________			Standard injection meter Detail

Name of Feeder				____________________________			Sr. No. 		_____________________________________

CT Ratio as per Name Plate		____________________________			Make		__________ Accuracy Class______________

CT Ratio Printed on Panel		_____________________________			Validity	_____________________________________

| Phase | Sr. No | Make | VA Burden | Accuracy Class |
| --- | --- | --- | --- | --- |
| R |  |  |  |  |
| Y |  |  |  |  |
| B |  |  |  |  |

| INJECTED VOLTAGE IN VOLTS | OUTPUT RATIO AND PHASE DISPLACEMENT |
| --- | --- |
|  | `R’ PHASE | `Y’ PHASE | `B’ PHASE |
|  | RATIO ERROR | PHASE DISPLACEMENT | RATIO ERROR | PHASE DISPLACEMENT | RATIO ERROR | PHASE DISPLACEMENT |
| 1 (120%) |  |  |  |  |  |  |  |
| 2 (100%) |  |  |  |  |  |  |  |
| 3 (20%) |  |  |  |  |  |  |  |
| 4 (5%) |  |  |  |  |  |  |  |
| Overall Ratio Error | _______% | _______% | _______% |
| Over All Phase Angle Error | _______% | _______% | _______% |
| Burden (as found) | ______VA | ______VA | ______VA |

OVERALL CTR 						____________________________________ERROR %	_________________

CONCLUSION							_______________________________________________________________

REMARKS							_________________________________________________________________

Rep. Of NPDL/BYPL/BRPL/NDMC/MES	                Rep. Of DTL

Sig.	_________________	                                 	    __________________

Name	________________                                     	    __________________

Deign.	_________________	                                  	    __________________

###### ANNEXURE – V

DISCREPANCY REPORT FOR THE INTERFACE INTRASTATE ABT METER

Meter No.:						_________________________

Location of installation:				_________________________

Date & Time of Checking:				_________________________

Voltage at the Panel at the time of the		_________________________

Checking:

| Date & Time Block | Voltage/Current Supply recorded at the meter terminal | Voltage/Current Supply recorded at the Field (CT/CVT MB) |
| --- | --- | --- |
|  | R-Phase Voltage | Y-Phase Voltage | B-Phase Voltage | R-Phase Current | Y-Phase Current | B-Phase Current |

REMARKS:

1. Any other findings noted by the site personnel.

2. Possible reasons for the discrepancy in the metering system.

NAME:  ___________________________

DESIGNATION:_____________________

COMPANY:__________________

###### ANNEXURE – VI

REQUEST TO BREAK SEALS

To :	[DTL/Interested Party] Date: [ ]

Tel:	[                       ]

Fax:	[                       ]

INTERESTED PARTY:__________________SERIAL NO:_______________

DETAILS OF WORK TO BE CARRIED OUT

We request for permission to carry out the work described below and to break such seals as are necessary.   We estimate the duration of the work to be from [              ] to [              ]

The work is to be carried out at site by [                            ].

The description of the work is as follows:

_________________________________________________________________________

_________________________________________________________________________

_________________________________________________________________________

The circuits and meters to be affected are as follows:

| CIRCUIT/METER ID | COMMENTS |
| --- | --- |

FROM:

Name______________________

Signature ___________________

Position________________________________ Date ______________________

###### ANNEXURE – VI

COMMENTS OF RECIPIENTS:

We acknowledge receipt of your request dated [                                          ].  We hereby [give/withhold]* consent.  Our reasons for withholding consent are [                         ].  Our representative dealing with sealing is [                         ].  He will/ will not be attending when the work is carried out.

By:

Name_____________________________ Signature _____________________________

Position____________________________ Date ____________________________________

CONFIRM COMPLETION OF WORK AND SEALS APPLIED:

DESCRIPTION OF COMPLETED WORK:

_____________________________________________________________________________

_____________________________________________________________________________

_____________________________________________________________________________

Name_____________________________ Signature _______________________________

Position____________________________ Date ____________________________________

(INTERESTED PARTY)

Name______________________________ Signature _______________________________

Position_____________________________Date ____________________________________

[* Delete as appropriate]

List of Metering points

| Sr. No. | METER NO. | FEEDER NAME |
| --- | --- | --- |
| 1 | 4864786 | 6.6 KV IRRIGATION PUMP |
| 2 | 4864789 | IP STATION BAY-9 |
| 3 | 4864792 | SUDHARSHAN PARK VISHAL |
| 4 | 4864794 | ROHTAK ROAD (FAIZ ROAD) |
| 5 | 4864795 | ROHTAK ROAD (DMS) |
| 6 | 4864796 | ROHTAK ROAD SB MILL-I |
| 7 | 4864797 | ROHTAK ROAD SB MILL-2 |
| 8 | 4864798 | NARAINA 16 MVA TX.-I |
| 9 | 4864799 | NARAINA 16 MVA TX.-2 |
| 10 | 4864801 | ROHTAK ROAD RAMPURA-I |
| 11 | 4864802 | ROHTAK ROAD SH. WALA BAGH-2 |
| 12 | 4864803 | AIIMS TX.-3 |
| 13 | 4864804 | RIDGE VALLEY KHYBER LANE-I EXP. |
| 14 | 4864807 | 20 MVA TX. KASHMIRI GATE |
| 15 | 4864808 | S MANDI (BG RD-1) |
| 16 | 4864818 | ROHTAK ROAD VISHAL-I |
| 17 | 4864819 | ROHTAK ROAD VISHAL-2 |
| 18 | 4864820 | ROHTAK ROAD RAMPURA-II |
| 19 | 4864824 | REWARI LINE 20 MVA TX. |
| 20 | 4864827 | Ridge Valley -Tx-1 |
| 21 | 4864828 | Ridge Valley -Tx-2 |
| 22 | 4864830 | NARAINA DMS |
| 23 | 4864831 | FOUNTAIN BAY-16 |
| 24 | 4864832 | MINTO ROAD BAY-17 |
| 25 | 4864833 | RPH TOWN HALL-3 |
| 26 | 4864834 | RPH LAHORI GATE-1 |
| 27 | 4864835 | RPH LAHORI GATE-2 |
| 28 | 4864836 | RPH JAMA MASJID-1 |
| 29 | 4864837 | RPH JAMA MASJID-2 |
| 30 | 4864838 | GB PANTH. (BAY-13) |
| 31 | 4864839 | RPH B-12 SACHIVALYA |
| 32 | 4864841 | S.MANDI (BGRD-2) |
| 33 | 4864842 | ROHTAK ROAD MADIPUR |
| 34 | 4864843 | SHASTRI PARK PUSA-1 |
| 35 | 4864844 | SHASTRI PARK PUSA-2 |
| 36 | 4864846 | NARAINA KIRBY PLACE-I |
| 37 | 4864847 | NARAINA KIRBY PLACE-2 |
| 38 | 4864848 | NARAINA KHYBER LANE-I |
| 39 | 4864849 | NARAINA KHYBER LANE-I |
| 40 | 4864850 | NARAINA (SHEKHAWATI) |
| 41 | 4864852 | RIDGE VALLEY SPM-2 |
| 42 | 4864880 | MVA TX.-1 |
| 43 | 4864881 | MVA TX.-2 |
| 44 | 4864882 | ROHTAK ROAD 16 MVA TX.-III |
| 45 | 4864883 | KAMLA Mkt-1 |
| 46 | 4864884 | RPH KAMLA Mkt- Tx-2 |
| 47 | 4864886 | NARAINA R.LINE-I |
| 48 | 4864887 | NARAINA R.LINE-2 |

| Sr. No. | METER NO. | FEEDER NAME |
| --- | --- | --- |
| 49 | 4864888 | NARAINA INDERPURI |
| 50 | 4864889 | KASHMIRI GATE CIVIL LINE-I |
| 51 | 4864890 | OKHLA TX.- 1 (33KV) |
| 52 | 4864891 | OKHLA TX.- 2 (33KV) |
| 53 | 4864893 | 50 MVA TX-3 PPG 33 |
| 54 | 4864902 | TX-1 P.STREET33) |
| 55 | 4864904 | GOPAL PUR TX.-1 |
| 56 | 4864905 | GOPALPUR TX.-3 |
| 57 | 4864906 | OKHLA TX.- 3 (33KV) |
| 58 | 4864907 | OKHLA TX.- 4 (33KV) |
| 59 | 4864908 | LODHI ROAD TX.-I |
| 60 | 4864909 | LODHI ROAD TX.-2 |
| 61 | 4864910 | KASHMIRI GATE 100MVA TR.-I |
| 62 | 4864911 | KASHMIRI GATE 100MVA TR.-II |
| 63 | 4864912 | SUBZI MANDI TX.-I |
| 64 | 4864913 | SUBZI MANDI TX.-2 |
| 65 | 4864914 | 100 MVA TX-1 PPG 33 |
| 66 | 4864915 | PPG TX-I |
| 67 | 4864916 | GEETA COLONY I/C-I |
| 68 | 4864917 | GEETA COLONY I/C-II |
| 69 | 4864918 | PPG 33KV TX-4 |
| 70 | 4864920 | DIAL Tx-2 |
| 71 | 4864935 | TX-2 P.STREET33) |
| 72 | 4864938 | DELHI-I |
| 73 | 4864939 | SHALIMARBAGH TX.-I |
| 74 | 4864940 | SHALIMAR BAGH TX.-2 |
| 75 | 4864943 | GT-66KV-AKSHAR- DHAM |
| 76 | 4864948 | BD MARG-1 P.STREET |
| 77 | 4864949 | PARK STREET B.D. MARG-2 |
| 78 | 4864951 | PARK STREET R. VALLEY-I |
| 79 | 4864953 | ROHINI TX.-3 |
| 80 | 4864954 | MANGOLPURI NANGLOI -I |
| 81 | 4864955 | MANGOLPURI NANGLOI -2 |
| 82 | 4864961 | Kanjhawala-66kv DMRC MUNDKA |
| 83 | 4864962 | TX-1 P.STREET 66 |
| 84 | 4864964 | OKHLA TX.-I (66KV) |
| 85 | 4864965 | OKHLA TX.- 2 (66KV) |
| 86 | 4864966 | MEHRAULI TX.-I |
| 87 | 4864967 | MEHRAULI TX.-2 |
| 88 | 4864968 | TX-1 S.O.W. |
| 89 | 4864969 | NAJAFGARH TX.-1 |
| 90 | 4864970 | NAJAFGARH TX.-2 |
| 91 | 4864971 | NAJAFGARH TX.-3 |
| 92 | 4864972 | NAJAFGARH TX.-4 |
| 93 | 4864973 | PAPPANKALAN TX.-I |
| 94 | 4864974 | PAPPANKALAN TX.-2 |
| 95 | 4864975 | PAPPANKALAN TX.-3 |
| 96 | 4864976 | PAPPANKALAN TX.-4 |
| 97 | 4864979 | VASANT KUNJ TX.-3 |
| 98 | 4864980 | TX-2 S.O.W. |
| 99 | 4864981 | TX-3 S.O.W. |

| Sr. No. | METER NO. | FEEDER NAME |
| --- | --- | --- |
| 100 | 4864982 | ROHINI TX.-I |
| 101 | 4864983 | ROHINI TX.-2 |
| 102 | 4864984 | ROHINI TX.-4 |
| 103 | 4864986 | TX-2 GZP |
| 104 | 4864988 | VASANT KUNJ TX.-I |
| 105 | 4864989 | VASANT KUNJ TX.-2 |
| 106 | 4864990 | SARITA VIHAR TX.-1 |
| 107 | 4864991 | SARITA VIHAR TX.-2 |
| 108 | 4864993 | TX-2 PPG 66 |
| 109 | 4865022 | DSIDC BAWANA |
| 110 | 4865024 | DIAL Tx-1 |
| 111 | 4865033 | TX-2 P.STREET 66 |
| 112 | 4865034 | NARELA TX.-I |
| 113 | 4865035 | NARELA TX.-2 |
| 114 | 4865037 | GT VIDYUT BHAWAN-1 |
| 115 | 4865038 | GT VIDYUT BHAWAN-2 |
| 116 | 4865039 | GT SCHOOL LANE-I |
| 117 | 4865040 | GT SCHOOL LANE-2 |
| 118 | 4865041 | GT (DMRC-I) |
| 119 | 4865042 | GT (DMRC-II) |
| 120 | 4865048 | MEHRAULI TX.-3 |
| 121 | 4865053 | TX-1 GZP |
| 122 | 4865054 | KANJHAWALA TX.-I |
| 123 | 4865055 | KANJHAWALA TX.-2 |
| 124 | 4865056 | BAWANA I/C |
| 125 | 4865057 | KASHMIRI GATE DMRC.-I |
| 126 | 4865058 | KASHMIRI GATE DMRC.-2 |
| 127 | 4865060 | Shalimar Bagh 220kv DMRC |
| 128 | 4865065 | SIGNAL ENCLAVE |
| 129 | 4865066 | R.R. HOSPITAL |
| 130 | 4865067 | DEFENCE CLUB |
| 131 | 4865076 | EXHIBITION -I (TILAK MARG) |
| 132 | 4865077 | EXHB.-I (KRISHI BHAWAN) |
| 133 | 4865078 | SUBROTO PARK |
| 134 | 4865079 | SUBROTO PARK |
| 135 | 4865080 | BI LINES |
| 136 | 4865081 | BI LINES |
| 137 | 4865086 | KASHMIRI GATE ISBT |
| 138 | 4865087 | REWARI LINE BUS I-2 |
| 139 | 4865088 | Najafgarh Local Tx-1 |
| 140 | 4865090 | VISHAL RAMESH NAGAR-I |
| 141 | 4865092 | NARAINA GOPINATH BAZAAR |
| 142 | 4865093 | LODHI ROAD SHAN NAGAR-I |
| 143 | 4865094 | LODHI ROAD SHAN NAGAR-2 |
| 144 | 4865095 | IP STATION BAY-25 |
| 145 | 4865096 | IP STATION BAY-7 |
| 146 | 4865097 | IP STATION BAY-37 |
| 147 | 4865098 | IP KAMLA MKT. B-18 |
| 148 | 4865099 | IP PANTT.HOSPITAL B-19 |
| 149 | 4865100 | B-31 (IG STD) |
| 150 | 4865101 | IP B-17 |

| Sr. No. | METER NO. | FEEDER NAME |
| --- | --- | --- |
| 151 | 4865102 | IP MINTO ROAD B-34 |
| 152 | 4865103 | AIIMS TX-1 |
| 153 | 4865124 | IP STATION BAY-2 |
| 154 | 4865125 | IP STATION BAY-4 |
| 155 | 4865126 | IP STATION BAY-6 |
| 156 | 4865127 | IP STATION BAY-10 |
| 157 | 4865128 | IP STATION BAY-16 |
| 158 | 4865129 | IP STATION BAY-28 |
| 159 | 4865130 | IP STATION BAY-38 |
| 160 | 4865131 | IP STATION BAY-42 |
| 161 | 4865132 | AIIMS TX.-2 |
| 162 | 4865133 | KIDWAI NAGAR 10 MVA TX. KILOKARI-2 |
| 163 | 4865134 | RIDGE VALLEY (S RD.-1) |
| 164 | 4865135 | RIDGE VALLEY (S RD.-2) |
| 165 | 4865136 | P.ST. (BAIRD RD-1) |
| 166 | 4865137 | P.ST. (BAIRED RD-2) |
| 167 | 4865138 | P.ST. (NIRMAN BHWN) |
| 168 | 4865139 | P.ST.(H.LANE) |
| 169 | 4865140 | RIDGE VALLEY SPM-I |
| 170 | 4865142 | RIDGE VALLEY NEHRU PARK |
| 171 | 4865143 | TILAK MARG EXHB-II |
| 172 | 4865144 | LODHI ROAD VIDYUT BHAWAN |
| 173 | 4865151 | IP STATION BAY-1 |
| 174 | 4865152 | IP STATION BAY-54 |
| 175 | 4865161 | IP KAMLA MKT. B-30 |
| 176 | 4865162 | IP IG STD. B-29 |
| 177 | 4865163 | RIDGE VALLEY KHYBER LANE-2 EXP. |
| 178 | 4865166 | IP STATION BAY-13 |
| 179 | 4865167 | 50 MVA TX-2 PPG 33 |
| 180 | 4865168 | ROHTAK ROAD SH. WALA BAGH-I |
| 181 | 4865169 | DMS (PANDAV NGR) |
| 182 | 4865170 | REWARI LINE (BUS COUPLER) |
| 183 | 4865179 | IP STATION BAY-5 LAJPAT NGR. |
| 184 | 4865180 | IP STATION BAY-24 |
| 185 | 4902492 | PRAGATI GT-I |
| 186 | 4902493 | PRAGATI GT-II |
| 187 | 4902494 | PRAGATI STG-3 |
| 188 | 4902497 | GT IBT-I |
| 189 | 4902498 | GT IBT-II |
| 190 | 4902500 | NARELA TX.-3 |
| 191 | 4902501 | (P.ST. R.V-II). EXP. |
| 192 | 4902502 | 66KV GHEBRA-LILO-MGP-NGL |
| 193 | 4902504 | DELHI-I |
| 194 | 4902505 | RPH IBT-I |
| 195 | 4902506 | RPH IBT-II |
| 196 | 4902507 | DELHI-I |
| 197 | 4902516 | REWARI LINE BUS 2-3 |
| 198 | 4902519 | VISHAL BALI NAGAR |
| 199 | 4902520 | VISHAL ESI HOSPITAL |
| 200 | 4902521 | SB MILL MOTI NAGAR |
| 201 | 4902522 | SB MILL 53 RAMA ROAD |

| Sr. No. | METER NO. | FEEDER NAME |
| --- | --- | --- |
| 202 | 4902523 | SB MILL BREAKFAST |
| 203 | 4902524 | SB MILL 70 RAMA ROAD |
| 204 | 4902525 | SB MILL MOTI NAGAR-II |
| 205 | 4902526 | SB MILL N.G. ROAD |
| 206 | 4902527 | SB MILL PHILIPS |
| 207 | 4902528 | SB MILL 70 zakhira |
| 208 | 4902529 | BG ROAD CSA |
| 209 | 4902530 | BG ROAD DCM-I |
| 210 | 4902531 | BG ROAD DCM-II |
| 211 | 4902532 | BG ROAD SADAR |
| 212 | 4902535 | DMS PHILIPS |
| 213 | 4902536 | DMS 69 NG ROAD |
| 214 | 4902537 | DMS J BLOCK KIRTI NAGAR |
| 215 | 4902538 | DMS H BLOCK KIRTI NAGAR |
| 216 | 4902539 | DMS SHADI KHAM PUR |
| 217 | 4902540 | DMS BREAKFAST |
| 218 | 4902541 | FAIZ ROAD TIBIA COLLEGE-I |
| 219 | 4902542 | FAIZ ROAD TIBIA COLLEGE-II |
| 220 | 4902543 | FAIZ ROAD TIBIA MANAKPURA |
| 221 | 4902544 | IP STATION 11KV IP-2 |
| 222 | 4902545 | BOOSTER PUMP |
| 223 | 4902556 | DSIDC BAWANA LOCAL |
| 224 | 4902563 | Najafgarh Local Tx-2 |
| 225 | 4902564 | Lodhi Rd. Local Tx-1 |
| 226 | 4902565 | Okhla. Local Tx-1 |
| 227 | 4902567 | Vasant Kunj. Local Tx-1 |
| 228 | 4902568 | K.Gate Local Tx-1 |
| 229 | 4902569 | Gazipur Local Tx-1 |
| 230 | 4902571 | 11KV BUS COUPLER KASHMIRI GATE |
| 231 | 4902572 | BUS COUPLER -3 NDPL |
| 232 | 4902577 | Bay-27 (Aux.FDR) IP |
| 233 | 4902579 | Bay-8 (Aux.FDR) IP |
| 234 | 4902583 | Bay-39 (Aux.FDR) IP |
| 235 | 4902585 | PPK-II. Local Tx-1(630kva) |
| 236 | 4902586 | -11KV VIKAS SADAN (AIIMS) |
| 237 | 4902587 | -11KV NDSE (AIIMS) |
| 238 | 4902588 | S.O.W. Local Tx-1 |
| 239 | 4902589 | PPK-I Local Tx-1 |
| 240 | 4902590 | Sarita Vihar. Local Tx-1 |
| 241 | 4902591 | Mehrauli Local Tx-1 |
| 242 | 4902593 | Patparganj. Local Tx-1 |
| 243 | 4902595 | Mehrauli Local Tx-2 |
| 244 | 4902596 | I.P.Ext. Local Tx-1 |
| 245 | 4902597 | Naraina. Local Tx-1 |
| 246 | 4902598 | Gopalpur. Local Tx-2 |
| 247 | 4902599 | Narela Local Tx-1 |
| 248 | 4902600 | Rohini Local Tx-1 |
| 249 | 4902601 | Shalimar Bagh Local Tx-1 |
| 250 | 4902602 | Kanjhawala. Local Tx-1 |
| 251 | 4902603 | Subzi Mandi. Local Tx-1 |
| 252 | 4902606 | Lodhi Rd. Local Tx-2 |

| Sr. No. | METER NO. | FEEDER NAME |
| --- | --- | --- |
| 253 | 4902611 | Patparganj. Local Tx-2 |
| 254 | 4962369 | GT (GAIL) |
| 255 | 5100228 | MUNDAKA 66 KV NDPL |
| 256 | 5128400 | Rohtak Road Kirti Nager |
| 257 | 5128402 | Naraina Inder Puri-2 |
| 258 | 5128405 | KASHMIRI GATE CIVIL LINE-2 |
| 259 | 5128410 | SHALIMARBAGH TX.-3 |
| 260 | 5128412 | DELHI-I |
| 261 | 5128414 | MASJID MOTH -33KV-I |
| 262 | 5128416 | MASJID MOTH -33KV-II |
| 263 | 5128432 | GOPALPUR |
| 264 | 5128434 | PARK STREET DMRC 66KV |
| 265 | 5128437 | PAPPANKALAN-II TX-1 |
| 266 | 5128439 | PAPPANKALAN-II TX.-2 |