## Sheet1
Self certification of UFRs and df/dt relays testing carried out by STUs for the Ist Quarter,2018-19 (April-18-June-18)
Name of State Control Area:Delhi
S.No. | Name of S/Stn (including voltage level) | Name of Feeder/ transformer (including voltage level) | Affected Area | Estimated Load relief(MW) | Minimum Load on the feeder (MW) | Whether the feeder is radial | Whether this feeder/underlying feeders are a part of scheduled power cuts/load shedding | Whether this feeder /under lying feeders covered under UFR | Whether this feeder /under lying feeders covered under df/dt shedding scheme | Whether the feeder/under lying feeders covered under any SPS? | UFR(Hz) or df/dt(Hz/sec.) setting | Whether power flow and breaker status of the feeder/underlying feeder visible in SLDC through SCADA | Whether relay is Numerical | Model and Make of relay | Date and time when relay/load relief /operation checked last time | Name and Dignation of the checking officer
1 | 220KV KASHMIRI GATE | 11KV I.S.B.T. Flyover |  | 1.4 | 0.39425 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 19.04.2017 (Actual Tripping) | Mr. Avishek Mallick, Asst. Manager
|  | 11KV New Kashmiri Gate |  | 2.7 | 0.49875 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Mahavir Icefactory |  | 1.8 | 0.76 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV G.P.O. |  | 0.3 | 0.54625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV Lohori Gate |  | 22.3 | 5 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Hamilton Road |  | 2.3 | 0.59375 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Bela Road |  | 2.3 | 0.19 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV Ludlocastle |  | 3.5 | 0.57 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV Jama Masjid |  | 18.3 | 5.5 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV Metcalf House |  | 1.4 | 0.76 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
2 | 220kV SOW | 66 KV YAMUNA VIHAR -1 |  | 50.3 | 12.54 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143, Alstom Make | 19.04.2017 (Actual Tripping) | Mr. Avishek Mallick, Asst. Manager
|  | 66 KV YAMUNA VIHAR -2 |  | 50.3 | 12.54 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 66 KV SHASTRI PARK-I |  | 26.3 | 10.26 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 66 KV SHASTRI PARK-II |  | 31.4 | 7.41 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV O/G TUKHMEERPUR |  | 2 | 0.40375 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV O/G B BLK. BHAJANPURA |  | 4.085 | 1.0212 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV O/G MONI BABA MANDIR |  | 2.1 | 0.3325 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV O/G SHAHDRA BANDH |  | 3.3 | 0.49875 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV O/G 3 1/2 PUSHTA VIJAY COLONY |  | 2.7 | 0.57 | Yes | No | No | yes | No | 48.8Hz | yes | yes
|  | 11KV O/G D-BLOCK GAWARI EXTN |  | 3 | 0.665 | Yes | No | No | yes | No | 48.8Hz | yes | yes
|  | 11KV O/G WAZIRABAD SWITCHING STATION-II |  | 2.1 | 0.26125 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV O/G SADATPUR |  | 4.6 | 1.235 | Yes | No | No | yes | No | 48.8Hz | yes | yes
3 | 220KV GEETA COLONY | 33KV KANTI NG.-I |  | 23.6 | 2.7006 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 19.04.2017 (Actual Tripping) | Mr Krishan Kumar, Asstt. Manager
|  | 33KV KANTI NG.-II |  | 8.8 | 3.4436 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV SHAKAR PUR |  | 21 | 2.1719 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV GEETA CLY-I |  | 19.8 | 3.8152 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV GEETA CLY-II |  | 20.4 | 7.0302 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV KAILASH CLY-I |  | 18.6 | 2 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV KAILASH CLY-II |  | 15 | 2 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
4 | 220KV PATPARGANJ | 66KV VIVEK VHR-I |  | 52 | 13 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes | P143, Alstom Make | 19.04.2017 (Actual Tripping) | Mr Krishan Kumar, Asstt. Manager
|  | 66KV VIVEK VHR-II |  | 52 | 13 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV GURU ANGAD NG.-I |  | 17.2 | 5.0726 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV GURU ANGAD NG.-II |  | 19.2 | 4.2867 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV CBD |  | 26 | 8.1447 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV PREET VHR |  | 31.7 | 5.8575 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV IDC |  | 2.0005 | 0.50011 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV COMMERCIAL |  | 2.8 | 0.4763 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV PREET VHR |  | 2.9 | 0.35 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV SHAKARPUR |  | 2.5 | 0.69063 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 33kV SHAKARPUR |  | 10.86 | [6 empty] | 48.4Hz | yes | yes
|  | 33kV GEETA COLONY |  | 9.46 | [6 empty] | 48.4Hz | yes | yes
|  | 33kV MOTHER DAIRY | [8 empty] | 48.4Hz | yes | yes
5 | 220KV NAJAFGARH | 66kv jaffar pur -I |  | 6.65 | 1.6625 | Yes | No | yes | No | No | 48.4Hz | yes | yes | P143, Alstom Make | 19.04.17 | Mrs. Twinkle Gupta, Asst. Manager
|  | 66KV jaffar pur -II |  | 26.61 | 6.6525 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 11kV Chhawala |  | 2.4 | 1.75 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kVRama Park |  | 1.85 | 0.4625 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kV Deenpur |  | 3.7 | 0.925 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 11kv TP KOTLA |  | 3.1 | 0.925 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv Nangli Sakarwati |  | 3 | 1.0625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv Anaj Mandi |  | 3.8 | 1.04 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kv Najafgarh-I |  | 4 | 1.3175 | Yes | No | No | yes | No | 49.0Hz | yes | yes
|  | 11kV Dhichau Kalan |  | 4.8 | 1.2 | Yes | No | No | yes | No | 48.6Hz | yes | yes
|  | 11kv Seven panel |  | 2.8 | 0.8325 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kv Kakrola |  | 2.4 | 1.385 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 66kV G-5 PPK-1 | [8 empty] | 48.4Hz | yes | yes
|  | 66kV G-5 PPK-2 | [8 empty] | 48.4Hz | yes | yes
6 | 220KV LODHI ROAD | 33KV nizamuddin |  | 31.4 | 2.7725 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 05.07.18 | Mr. Yashwant Singh Rawat, Asstt. Manager
|  | 33KV J.L.N. Stadium |  | 1.7 | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV Defence colony-II |  | 5.7 | 6.375 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV India habitat cen-I |  | ON | #VALUE! | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV India habitat cen-II |  | 3.1 | 0.9425 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33kv vidut bhawan |  | 11.4 | 1.385 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV Scope Bldg.16 |  | 3.1 | 0.6475 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV NBCC |  | 1.3 | 0.415 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Scope Bldg.15 |  | 2.22 | 0.555 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Institutional Area |  | 1.7 | 0.4625 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Defence colony Flyover |  | 3.51 | 0.8775 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Lodhi Cly. |  | 2.1 | 0.23 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV NBCC East Block |  | 1.7 | 0.555 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
7 | 220KV SARITA VIHAR | 66KV MATHURA ROAD |  | 67.4 | 5.5 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143, Alstom Make | 21.02.18 (Actual Tripping) | Mr Mohd. Ansaar, Asstt. Manager
|  | 11KV ALLI VILLAGE |  | 4.2 | 0.9526 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV JAIT PUR |  | 5 | 0.71445 | Yes | No | yes | No | No | 49.0Hz | yes | yes
8 | 220KV NARAINA | 33KV Rewari line-I |  | 13.2 | 5.8225 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 18.04.17 | Ms. Twinkle Gupta, Asst. Manager
|  | 33KV Payal |  | 23.29 | 5.8225 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kv naraina |  | 1.3 | 0.855 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV A BLKshop. Complex |  | 2.24 | 0.56 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kv Magoo-I |  | 2.68 | 0.67 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kv Magoo-II |  | 1.94 | 0.485 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33kV Khyber Lane-I |  | 12.2 | [6 empty] | 49.2Hz | yes | yes
|  | 33kV Khyber Lane-II |  | 11.2 | [6 empty] | 49.2Hz | yes | yes
|  | 33kV Inderpuri-I | [8 empty] | 48.8Hz | yes | yes
|  | 33kV Inderpuri-II | [8 empty] | 48.8Hz | yes | yes
9 | 220KV KANJHAWALA | 11KV Punjab Khera |  | 3.1 | 0.54 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 20.04.17 | Mr. Amit Garg, Asst. Manager
|  | 11kv O/H Rani khera |  | 3.4 | 0.975 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kv ABC Kanjhawala |  | 2.5 | 0.9 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv S.O.S. Bawana |  | 2.6 | 0.0175 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV U/G Kanjhwala |  | 3.7 | 1.0575 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kv O/H Kanjhawala |  | 2.4 | 0.8925 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kV ABC Rani Kheda |  | 2.6 | 0.7475 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11kv Ghewra |  | 2.5 | 0.8 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 66kV Pooth Khurd |  | 29.2 | [6 empty] | 49.2Hz | yes | yes
|  | 66kV RG-23 Ckt.1 |  | 38.9 | [6 empty] | 48.4Hz | yes | yes
10 | 220KV IP Station | 33kv Exhibition -I |  | 6.86 | 1.715 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 15.01.18 | Mohd. Ansaar, Asstt. Manager
|  | 33kv Exhibition -2 |  | 15.72 | 3.93 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV BAY-24 |  | 11.43 | 2.8575 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV BAY-30 |  | 11 | [6 empty] | 48.6Hz | yes | yes
11 | 220KV RPH | 33KV JAMA MASJID-1 |  | 7 | 1.75 | Yes | No | yes | No | No | 48.4Hz | yes | yes | P143, Alstom Make | 30.06.18 | Mohd. Ansaar, Asstt. Manager
|  | 33KV JAMA MASJID-2 |  | 7 | 1.75 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 33KV LAHORI GATE-1 |  | 6.3 | 1.575 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 33KV Fountain |  | 14.9 | 3.725 | Yes | No | yes | No | No | 48.4Hz | yes | yes
12 | 220KV MASJID MOTH | 33KV BALAJI |  | 12.5 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 21.02.18 (Actual Tripping) | Mr Jain Kumar, Asstt. Manager
|  | 33KV PUSHPA VIHAR |  | 7.7 | 3.285 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV SHIVALIK |  | 30.9 | 7.86 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
13 | 400KV MUNDKA | 66KV GHEVRA |  | 35 | 8.75 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 07.05.17 | Ms. Twinkle Gupta, Asst. Manager
|  | 66KV MANGOLPURI |  | 49 | 12.25 | Yes | No | yes | No | No | 48.6Hz | yes | yes
14 | 220KV PPK-2 | 66KV G-15 DWARKA CKT-2 |  | 50.3 | 10.0025 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes | P143, Alstom Make | 19.04.17 | Ms. Twinkle Gupta, Asst. Manager
|  | 66KV G-15 DWARKA CKT-1 |  | 50.3 | 10.86 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 66kV G-5 Matiyala-1 |  | 56 | [6 empty] | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 66kV G-5 Matiyala-2 |  | 56 | [6 empty] | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 66kV G-4 Dwarka Ckt.1 | [8 empty] | 48.4Hz | yes | yes
|  | 66kV G-4 Dwarka Ckt.2 | [8 empty] | 48.4Hz | yes | yes
15 | 220KV NARELA | 66KV BADLI-I |  | 15.9 | 8.315 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 27.04.17 | Mr. Praveen Kumar, Asst. Manager
|  | 66KV BADLI-II |  | 15.9 | 8.315 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV BHALASWA-I |  | 59.7 | 11.7825 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 66KV BHALASWA-II |  | 59.7 | 11.7825 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11kv U/G NARELA |  | 3.86 | 0.965 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 11KV NARELA O/H |  | 3.47 | 0.8675 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 11KV DDA-4 |  | 1 | 0.25 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 11kv DDA-5 |  | 0.89 | 0.2225 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 11kv BAWANA |  | 1.7 | 0.475 | Yes | No | yes | No | No | 48.6Hz | yes | yes
16 | 220KV SHALIMARHBAGH | 33KV RANI BAGH -1 |  | 6.4 | 3.05 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143, Alstom Make | 12.05.17 | Mr. Avishek Mallick, Asst. Manager
|  | 33KV RANI BAGH -2 |  | 6.7 | 3.05 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 33KV SMB KHOSLA U/G-1 |  | 7.9 | 3.305 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV SMB Facility Centre-II |  | 13.8 | 2.4225 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 33KV SMB KHOSLA O/H-2 |  | 8.9 | 6.3425 | Yes | No | No | yes | No | 48.4Hz | yes | yes
|  | 33KV WAZIRPUR-1 |  | 10.5 | 5.6425 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV WAZIRPUR -2 |  | 19.04 | 4.76 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV VILLAGE BADLI-2 |  | 2.4 | 0.513 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV 10- B SMB |  | 2.09 | 0.5225 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV KU PPR |  | 1.2 | 0.4275 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV 11-B SMB |  | 2.1 | 0.5605 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV FU S/Stn PPR |  | 2.5 | 0.79325 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV O/H HYD. DISP. |  | 1.1 | 0.3515 | [5 empty] | 49.0Hz | yes | yes
17 | 220KV ROHINI | 66KV Rohini-VI CKT-I |  | 0 | 0 | Yes | No | yes | No | No | 48.4Hz | yes | yes | P143, Alstom Make | 24.04.17 | Mr. Praveen Kumar, Asst. Manager
|  | 66KV Rohini-VI CKT-II |  | 0 | 0 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 66KV ROHINI -IV CKT.I |  | 31.7 | 7.485 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV ROHINI -IV CKT.I |  | 31.7 | 7.485 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66kV Rohini-24 Ckt.1 |  | 48.7 | [6 empty] | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 66kV Rohini-24 Ckt.2 |  | 48.7 | [6 empty] | Below 49.9 Hz (SLOPE 0.3) | yes | yes
18 | 220KV DSIDC BAWANA | 66KV NARELA-1 |  | 30.9 | 7 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143, Alstom Make | 25.04.17 | Mr. Praveen Kumar, Asst. Manager
|  | 66KV NARELA-2 |  | 30.9 | 7 | Yes | No | yes | No | No | 48.6Hz | yes | yes
19 | 220KV VASANT KUNJ | 66KV RIDGE VALLEY-I |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 06.07.18 | Mr Jatin Kumar, Asstt. Manager
|  | 66KV RIDGE VALLEY-II |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV VASANT KUNJ C-I |  | 56 | 11.505 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 66KV VASANT KUNJ C-II |  | 56 | 11.7825 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV RANGPURI |  | 3.1 | 0.715 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV AB HOTEL |  | 1.7 | 0.3475 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV C9 VASANT KUNJ S/S 2 |  | 0.9 | 0.1375 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV C9 VASANT KUNJ S/S 5 |  | 0.7 | 0.23 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV NANGAL DAIRY |  | 2.7 | 0.0225 | Yes | No | yes | No | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV C8 VASANT KUNJ S/S-I |  | 0.65 | 0.1625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
20 | 220KV OKHLA | 33kV EAST OF KAILASH |  | 15.2 | 11.0875 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 05.07.18 | Mr Yashwant Singh Rawat, Asstt. Manager
|  | 66KV MALVIYA NGR-I |  | 32 | 6.0975 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 66KV MALVIYA NGR-II |  | 32 | 6.0975 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 33KV ALAKNANDA-2 |  | 20.9 | 3.1875 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 33KV BALAJI-I |  | 12.2 | 3.05 | Yes | No | No | yes | No | 48.4Hz | yes | yes
|  | 33KV BALAJI-II |  | 11.64 | 2.91 | Yes | No | No | yes | No | 48.4Hz | yes | yes
|  | 33KV MASJID MOTH |  | 17.4 | 3.1875 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV NEHRU PLACE-IV |  | 14.9 | 3.6025 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV NEHRU PLACE-I |  | 11.64 | 2.91 | Yes | No | No | yes | No | 48.4Hz | yes | yes
|  | 33KV NEHRU PLACE-II |  | 15.52 | 3.88 | Yes | No | No | yes | No | 48.4Hz | yes | yes
|  | 33KV TUGHLAKABAD |  | 24.3 | 6.0975 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
21 | 220KV MEHRAULI | 66KV VASANT KUNJ D-I |  | 0 | 0 | Yes | No | yes | No | No | 48.4Hz | yes | yes | P143, Alstom Make | 06.07.18 | Mr Jatin Kumar, Asstt. Manager
|  | 66KV VASANT KUNJ D-II |  | 0 | 0 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 66KV VASANT KUNJ C-I |  | 17.85 | 4.4625 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 66KV VASANT KUNJ C-II |  | 17.41 | 4.3525 | Yes | No | yes | No | No | 48.4Hz | yes | yes
|  | 66KV MALVIYA NAGAR-I |  | 34.1 | 10.4775 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV MALVIYA NAGAR-II |  | 36.7 | 12.28 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV I/C NO. 1 |  | 7.7 | 1.57 | Yes | No | No | yes | No | 49.0Hz | yes | yes
|  | 11KV I/C NO. 2 |  | 7.2 | 1.8 | Yes | No | No | yes | No | 48.4Hz | yes | yes
22 | 220KV PARKSTREET | 33KV PRASAD NAGAR |  | 16 | 7.1445 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143, Alstom Make | 12.07.18 (Actual Tripping) | Ms Ramneet Chanana, Asstt. Manager
|  | 66KV RIDGE VALLEY-1 |  | 25.1486 | 6.2872 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV RIDGE VALLEY-2 |  | 18.8615 | 4.7154 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66kV SHASTRI PARK-1 |  | 45 | [6 empty] | 49.0Hz | yes | yes
|  | 66kV SHASTRI PARK-2 |  | 45 | [6 empty] | 49.0Hz | yes | yes
23 | 220KV GAZIPUR | 66KV VIVEK VIHAR-I |  | 38.6 | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 21.02.18 (Actual Tripping) | Mr Krishan Kumar, Asstt. Manager
|  | 66KV VIVEK VIHAR-II |  | 48.6 | 13.25 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV KONDLI-I |  | 24 | 9 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV KONDLI-II |  | 22.3 | 8.5 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV FISH MKT.-II |  | 0 | 0.29 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV FISH MKT.-I |  | 0.3 | 0.06 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV TELCO-I |  | 0 | 0 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV TELCO-II |  | 0.1 | 0.0375 | Yes | No | yes | No | No | 48.6Hz | yes | yes
24 | 220kV PEERAGARHI | 33kV Sudarshan Park |  | 0 | [6 empty] | 48.4Hz | yes | yes | P143, Alstom Make | 26.11.16 | Mr. Amit Garg,Asst. Manager
|  | 33kV Rani Bagh |  | 14 | [6 empty] | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 33kV Vishal |  | 10.7 | [6 empty] | 48.8Hz | yes | yes
|  | 33kV Paschim Vihar A-4 |  | 24.1 | [6 empty] | 48.8Hz | yes | yes
|  | 33kV Udyog Nagar |  | 21 | [6 empty] | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 33kV Peeragarhi-1 |  | 0 | [6 empty] | 49.2Hz | yes | yes
|  | 33kV Peeragarhi-2 |  | 19 | [6 empty] | 49.2Hz | yes | yes
|  | 33kV Paschim Puri-1 |  | 20.4 | [6 empty] | 48.6Hz | yes | yes
|  | 33kV Paschim Puri-2 |  | 15.6 | [6 empty] | 48.6Hz | yes | yes
|  | 33kV Madipur |  | 21 | [6 empty] | 49.2Hz | yes | yes